## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.4a based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number
Date | 2017-11-22 10:58:29
Manufacturer Name | ABB
Product Name | TRIO solar inverter
Product Models | TRIO-50.0-TL-OUTD, TRIO-50.0-TL-OUTD-US-480 TRIO-50.0-TM-OUTD, TRIO-50.0-TM-OUTD-US-480, TRIO-60.0-TM-OUTD, TRIO-60.0-TM-OUTD-US-480
Product Description | Three Phase String Inverter consisting of three separable units: Power Module, DC Wiring Box; AC Wiring Box

## Versioning
Logical device for server: | Supervisor
Version | Change Log | Author of Change | Date of Change | Minimum reference FW version
0 | - First version | Andrea Botarelli | 2017-11-30 | C031
1 | - Updated conformance notes for register "Options" of M1 | Andrea Botarelli | 2017-12-04 | C031
2 | - Introduced conformance notes for specific use of "WinTms" register on M126 and M132. | Andrea Botarelli | 2017-12-05 | C031
3 | - Introduced conformance notes for specific use of "VArMaxQ<1-4>" registers on M121. | Andrea Botarelli | 2017-12-14 | C031
4 | - Review on "Versioning" sheet. The following info were introduced: - "Logical device for server" - "Minimum reference FW version" | Andrea Botarelli | 2017-12-15 | C031
5 | - Introduced conformance notes for specific use of "ModEna" register on M139 and M140. | Andrea Botarelli | 2017-12-21 | C031
6 | - Set "BLOWN FUSE" flag as unimplemented "DcEvt" register for on M160. | Andrea Botarelli | 2018-01-10 | C031
7 | - Extended conformance notes for specific use of "VArMaxQ<1-4>" registers on M121. | Andrea Botarelli | 2018-01-12 | C031
8 | - Corrected bitfield specification for "EvtVnd3" register on M103. | Andrea Botarelli | 2018-01-17 | C031
9 | - Added conformance notes for monotony of curve in M126 and M132. | Andrea Botarelli | 2018-01-19 | C031
10 | - Added conformance notes for specific use of "RvrtTms" register on M123. | Andrea Botarelli | 2018-01-28 | C031
11 |  |  | 2018-02-07 11:44
12 |  |  | 2018-02-07 11:44
13 |  |  | 2018-02-07 11:44
14 |  |  | 2018-02-07 11:44
15 |  |  | 2018-02-07 11:44
16 |  |  | 2018-02-07 11:44
17 |  |  | 2018-02-07 11:44
18 |  |  | 2018-02-07 11:44
19 |  |  | 2018-02-07 11:44
20 |  |  | 2018-02-07 11:44
21 |  |  | 2018-02-07 11:44
22 |  |  | 2018-02-07 11:44
23 |  |  | 2018-02-07 11:44
24 |  |  | 2018-02-07 11:44
25 |  |  | 2018-02-07 11:44
26 |  |  | 2018-02-07 11:44
27 |  |  | 2018-02-07 11:44
28 |  |  | 2018-02-07 11:44
29 |  |  | 2018-02-07 11:44
30 |  |  | 2018-02-07 11:44
31 |  |  | 2018-02-07 11:44
32 |  |  | 2018-02-07 11:44
33 |  |  | 2018-02-07 11:44
34 |  |  | 2018-02-07 11:44
35 |  |  | 2018-02-07 11:44
36 |  |  | 2018-02-07 11:44
37 |  |  | 2018-02-07 11:44
38 |  |  | 2018-02-07 11:44
39 |  |  | 2018-02-07 11:44
40 |  |  | 2018-02-07 11:44
41 |  |  | 2018-02-07 11:44
42 |  |  | 2018-02-07 11:44
43 |  |  | 2018-02-07 11:44
44 |  |  | 2018-02-07 11:44
45 |  |  | 2018-02-07 11:44
46 |  |  | 2018-02-07 11:44
47 |  |  | 2018-02-07 11:44
48 |  |  | 2018-02-07 11:44
49 |  |  | 2018-02-07 11:44
50 |  |  | 2018-02-07 11:44
51 |  |  | 2018-02-07 11:44
52 |  |  | 2018-02-07 11:44
53 |  |  | 2018-02-07 11:44
54 |  |  | 2018-02-07 11:44
55 |  |  | 2018-02-07 11:44
56 |  |  | 2018-02-07 11:44
57 |  |  | 2018-02-07 11:44
58 |  |  | 2018-02-07 11:44
59 |  |  | 2018-02-07 11:44
60 |  |  | 2018-02-07 11:44
61 |  |  | 2018-02-07 11:44
62 |  |  | 2018-02-07 11:44
63 |  |  | 2018-02-07 11:44
64 |  |  | 2018-02-07 11:44
65 |  |  | 2018-02-07 11:44
66 |  |  | 2018-02-07 11:44
67 |  |  | 2018-02-07 11:44
68 |  |  | 2018-02-07 11:44
69 |  |  | 2018-02-07 11:44
70 |  |  | 2018-02-07 11:44
71 |  |  | 2018-02-07 11:44
72 |  |  | 2018-02-07 11:44
73 |  |  | 2018-02-07 11:44
74 |  |  | 2018-02-07 11:44
75 |  |  | 2018-02-07 11:44
76 |  |  | 2018-02-07 11:44
77 |  |  | 2018-02-07 11:44
78 |  |  | 2018-02-07 11:44
79 |  |  | 2018-02-07 11:44
80 |  |  | 2018-02-07 11:44
81 |  |  | 2018-02-07 11:44
82 |  |  | 2018-02-07 11:44
83 |  |  | 2018-02-07 11:44
84 |  |  | 2018-02-07 11:44
85 |  |  | 2018-02-07 11:44
86 |  |  | 2018-02-07 11:44
87 |  |  | 2018-02-07 11:44
88 |  |  | 2018-02-07 11:44
89 |  |  | 2018-02-07 11:44
90 |  |  | 2018-02-07 11:44
91 |  |  | 2018-02-07 11:44
92 |  |  | 2018-02-07 11:44
93 |  |  | 2018-02-07 11:44
94 |  |  | 2018-02-07 11:44
95 |  |  | 2018-02-07 11:44
96 |  |  | 2018-02-07 11:44
97 |  |  | 2018-02-07 11:44
98 |  |  | 2018-02-07 11:44
99 |  |  | 2018-02-07 11:44
100 |  |  | 2018-02-07 11:44

## Testing Info
Submitter | Andrea Botarelli
Email | andrea.botarelli@it.abb.com
Phone
Interface Type | RTU
Baud Rate | 19200
Slave Id | 1

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | ABB | R
40020 | Model (Md) |  |  | -3P36- | R | Provided Md string is the part number of the specific model: - 3P54 = TRIO-TM-50.0-400 - 3P36 = TRIO-TM-60.0-480 - 3P45 = TRIO-TM-60.0-480-US
40036 | Options (Opt) |  |  | 0x015C/E/ | R | Provided Opt string is formatted as a list of string fields separated by '/' character: - Field 1: Model identifier formatted as [IDH + IDL] where IDL is the LSB and IDH is the MSB of the identifier. If one of the ID bytes is not-printable then they will be both presented as hexadecimal values preceded by "0x" string; if both ID bytes are printable then they will be presented with the corresponding ASCII characters. - Field 2: Country code formatted as [IDH + IDL] where IDL is the LSB and IDH is the MSB of the identifier. If one of the ID bytes is not-printable then they will be both presented as hexadecimal values preceded by "0x" string; if both ID bytes are printable then they will be presented with the corresponding ASCII characters.
40044 | Version (Vr) |  |  | 1747D | R | Provided SW release version string is formatted as [Y + WY + DW] where Y is the release year (format YY), WY is the release week of the year (format WW) and DW is the release day of the week (encoded as a single ASCII character starting from 'A' which is associated to Monday)
40052 | Serial Number (SN) |  |  | 120984-3P36-4317 | R | Provided serial number string is formatted as [SN + PN + WY] where SN is the internal serial number of the unit, PN is the internal part number of the unit and WY is the manufacturing week/year date expressed in WWYY format.
40068 | Device Address (DA) |  |  | 1 | RW
40069 | Pad |  |  |  | R

## 103
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 103
40071 | L |  |  | 50
40072 | Amps (A) |  |  | supported | R
40073 | Amps PhaseA (AphA) |  |  | supported | R
40074 | Amps PhaseB (AphB) |  |  | supported | R
40075 | Amps PhaseC (AphC) |  |  | supported | R
40076 | A_SF |  |  | -1 | R
40077 | Phase Voltage AB (PPVphAB) |  |  | supported | R
40078 | Phase Voltage BC (PPVphBC) |  |  | supported | R
40079 | Phase Voltage CA (PPVphCA) |  |  | supported | R
40080 | Phase Voltage AN (PhVphA) |  |  | supported | R
40081 | Phase Voltage BN (PhVphB) |  |  | supported | R
40082 | Phase Voltage CN (PhVphC) |  |  | supported | R
40083 | V_SF |  |  | -1 | R
40084 | Watts (W) |  |  | supported | R
40085 | W_SF |  |  | 1 | R
40086 | Hz |  |  | supported | R
40087 | Hz_SF |  |  | -2 | R
40088 | VA |  |  | supported | R
40089 | VA_SF |  |  | 1 | R
40090 | VAr |  |  | supported | R
40091 | VAr_SF |  |  | 1 | R
40092 | PF |  |  | supported | R
40093 | PF_SF |  |  | -4 | R
40094 | WattHours (WH) |  |  | unimplemented | R
40096 | WH_SF |  |  | 1 | R
40097 | DC Amps (DCA) |  |  | supported | R
40098 | DCA_SF |  |  | -1 | R
40099 | DC Voltage (DCV) |  |  | unimplemented | R | For this product the DC voltage is not provided with model 103 but using model 160.
40100 | DCV_SF |  |  | unimplemented | R
40101 | DC Watts (DCW) |  |  | supported | R
40102 | DCW_SF |  |  | 1 | R
40103 | Cabinet Temperature (TmpCab) |  |  | supported | R | This measure is implemented as internal DC wiring-box temperature.
40104 | Heat Sink Temperature (TmpSnk) |  |  | supported | R | This measure is implemented as DC/AC (inverter) stage heatsink temperature.
40105 | Transformer Temperature (TmpTrns) |  |  | unimplemented | R
40106 | Other Temperature (TmpOt) |  |  | supported | R | This measure is implemented as external ambient temperature.
40107 | Tmp_SF |  |  | -1 | R
40108 | Operating State (St) |  |  | supported | R
|  |  | Off (OFF) | supported |  | This state corresponds to startup phase of inverter controller.
|  |  | Sleeping (SLEEPING) | supported |  | This state corresponds to execution of grid interface "auto-test" required by Italian country standard.
|  |  | Starting (STARTING) | supported |  | This state corresponds to grid connection phase.
|  |  | MPPT | supported |  | This state corresponds to inverter connected to grid and running with MPPT.
|  |  | Throttled (THROTTLED) | supported |  | This state corresponds to inverter connected to grid and running with limited active power (derating).
|  |  | Shutting down (SHUTTING_DOWN) | supported |  | This state corresponds to forced disconnection from grid (e.g. commanded by user through "remote off" command).
|  |  | Fault (FAULT) | supported |  | This state corresponds to fault causing disconnection from grid.
|  |  | Standby (STANDBY) | supported |  | This state corresponds to disconnection from grid caused by missing DC source or AC grid.
40109 | Vendor Operating State (StVnd) |  |  | supported | R
40110 | Event1 (Evt1) |  |  | supported | R
|  |  | Ground fault (GROUND_FAULT) | supported |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
|  |  | DC over voltage (DC_OVER_VOLT) | supported |  | This state corresponds to the following internal alarms: - E002: Input OV
|  |  | AC disconnect open (AC_DISCONNECT) | unimplemented
|  |  | DC disconnect open (DC_DISCONNECT) | unimplemented
|  |  | Grid shutdown (GRID_DISCONNECT) | supported |  | This state corresponds to grid absence.
|  |  | Cabinet open (CABINET_OPEN) | unimplemented
|  |  | Manual shutdown (MANUAL_SHUTDOWN) | supported |  | This state corresponds to the following internal alarms: - E035: Remote off
|  |  | Over temperature (OVER_TEMP) | supported |  | This state corresponds to the following internal alarms: - E014: OTH
|  |  | Frequency above limit (OVER_FREQUENCY) | supported |  | This state corresponds to the following internal alarms: - E006: Grid OF
|  |  | Frequency under limit (UNDER_FREQUENCY) | supported |  | This state corresponds to the following internal alarms: - E007: Grid UF
|  |  | AC Voltage above limit (AC_OVER_VOLT) | supported |  | This state corresponds to the following internal alarms: - E003: Grid OV
|  |  | AC Voltage under limit (AC_UNDER_VOLT) | supported |  | This state corresponds to the following internal alarms: - E004: Grid UV
|  |  | Blown String fuse on input (BLOWN_STRING_FUSE) | unimplemented
|  |  | Under temperature (UNDER_TEMP) | supported |  | This state corresponds to the following internal alarms: - E033: UTH
|  |  | Generic Memory or Communication error (internal) (MEMORY_LOSS) | supported |  | This state corresponds to statistics memory fault.
|  |  | Hardware test failure (HW_TEST_FAILURE) | supported |  | This state corresponds to the following internal alarms: - E005: Internal bus fault - E013: Wrong DC input mode - E019: Lekage current self-test fault - E020: Grid interface self-test fault - E021: Grid interface self-test fault - E053: Arc-fault detector self-test fault - E078: R-iso self-test fault
40112 | Event Bitfield 2 (Evt2) |  |  | supported | R
40114 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | supported | R | This register provides status of active power derating: - Bit0: Power curtailment from external command - Bit1: Power limitation from Frequency-Watt - Bit2: Power limitation from high average grid voltage - Bit3: Power limitation from anti-islanding protection - Bit4: Power limitation from grid current rating limitation - Bit5: Power limitation for high temperature - Bit6: Power limitation for high DC voltage - Bit7: Reserved - Bit8: Power limitation from ramp-rate (connection ramp) - Bit9: Power limitation from momentary cessation - Bit10: Power limitation from ramp-rate (normal ramp-up) - Bit11: Power limitation from Volt-Watt - Bit12-31: Reserved
40116 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | supported | R | This register provides status of apparent power derating: - Bit0: Power limitation for high temperature - Bit1: Power limitation for high DC voltage - Bit2-31: Reserved
40118 | Vendor Event Bitfield 3 (EvtVnd3) |  |  | supported | R | This register provides status of auxiliary devices: - Bit0: Fan fault - Bit1: Statistics memory fault - Bit2: RTC clock not set - Bit3: Reserved - Bit4: RTC low battery fault - Bit5: RTC quartz fault - Bit6-31: Reserved
40120 | Vendor Event Bitfield 4 (EvtVnd4) |  |  | supported | R | Fixed to 0 (reserved for future use)

## 120
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40122 | ID |  |  | 120
40123 | L |  |  | 26
40124 | DERTyp |  |  | supported | R
|  |  | PV | supported
|  |  | PV_STOR | supported
40125 | WRtg |  |  | supported | R
40126 | WRtg_SF |  |  | 1 | R
40127 | VARtg |  |  | supported | R
40128 | VARtg_SF |  |  | 1 | R
40129 | VArRtgQ1 |  |  | supported | R
40130 | VArRtgQ2 |  |  | supported | R
40131 | VArRtgQ3 |  |  | supported | R
40132 | VArRtgQ4 |  |  | supported | R
40133 | VArRtg_SF |  |  | 1 | R
40134 | ARtg |  |  | supported | R | Used as reference rating for current ramp-rate on M145.
40135 | ARtg_SF |  |  | 0 | R
40136 | PFRtgQ1 |  |  | supported | R
40137 | PFRtgQ2 |  |  | supported | R
40138 | PFRtgQ3 |  |  | supported | R
40139 | PFRtgQ4 |  |  | supported | R
40140 | PFRtg_SF |  |  | -3 | R
40141 | WHRtg |  |  | unimplemented | R
40142 | WHRtg_SF |  |  | unimplemented | R
40143 | AhrRtg |  |  | unimplemented | R
40144 | AhrRtg_SF |  |  | unimplemented | R
40145 | MaxChaRte |  |  | unimplemented | R
40146 | MaxChaRte_SF |  |  | unimplemented | R
40147 | MaxDisChaRte |  |  | unimplemented | R
40148 | MaxDisChaRte_SF |  |  | unimplemented | R
40149 | Pad |  |  |  | R

## 121
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40150 | ID |  |  | 121
40151 | L |  |  | 30
40152 | WMax |  |  | supported | RW
40153 | VRef |  |  | unimplemented | RW
40154 | VRefOfs |  |  | unimplemented | RW
40155 | VMax |  |  | unimplemented | RW
40156 | VMin |  |  | unimplemented | RW
40157 | VAMax |  |  | supported | RW
40158 | VArMaxQ1 |  |  | supported | RW | Since reactive power limit is equally applied on all quadrants, the same parameter value is actually exposed on VArMaxQ1, VArMaxQ2, VArMaxQ3 and VArMaxQ4. This produces the following consequences: - When one of these registers is written, the same value (if accepted) will be read on the others; - When multiple registers are written, only the last change is applied; In addition, if VArMax is changed when VArPct control (M123) is enabled in VArMax mode, it is necessary to disable and enable again the VArPct control or restart the logical controller (e.g. cycling power feed) in order to use the new VArMax limit.
40159 | VArMaxQ2 |  |  | supported | RW | Since reactive power limit is equally applied on all quadrants, the same parameter value is actually exposed on VArMaxQ1, VArMaxQ2, VArMaxQ3 and VArMaxQ4. This produces the following consequences: - When one of these registers is written, the same value (if accepted) will be read on the others; - When multiple registers are written, only the last change is applied; In addition, if VArMax is changed when VArPct control (M123) is enabled in VArMax mode, it is necessary to disable and enable again the VArPct control or restart the logical controller (e.g. cycling power feed) in order to use the new VArMax limit.
40160 | VArMaxQ3 |  |  | supported | RW | Since reactive power limit is equally applied on all quadrants, the same parameter value is actually exposed on VArMaxQ1, VArMaxQ2, VArMaxQ3 and VArMaxQ4. This produces the following consequences: - When one of these registers is written, the same value (if accepted) will be read on the others; - When multiple registers are written, only the last change is applied; In addition, if VArMax is changed when VArPct control (M123) is enabled in VArMax mode, it is necessary to disable and enable again the VArPct control or restart the logical controller (e.g. cycling power feed) in order to use the new VArMax limit.
40161 | VArMaxQ4 |  |  | supported | RW | Since reactive power limit is equally applied on all quadrants, the same parameter value is actually exposed on VArMaxQ1, VArMaxQ2, VArMaxQ3 and VArMaxQ4. This produces the following consequences: - When one of these registers is written, the same value (if accepted) will be read on the others; - When multiple registers are written, only the last change is applied; In addition, if VArMax is changed when VArPct control (M123) is enabled in VArMax mode, it is necessary to disable and enable again the VArPct control or restart the logical controller (e.g. cycling power feed) in order to use the new VArMax limit.
40162 | WGra |  |  | supported | RW
40163 | PFMinQ1 |  |  | unimplemented | RW
40164 | PFMinQ2 |  |  | unimplemented | RW
40165 | PFMinQ3 |  |  | unimplemented | RW
40166 | PFMinQ4 |  |  | unimplemented | RW
40167 | VArAct |  |  | unimplemented | RW
|  |  | SWITCH | supported
|  |  | MAINTAIN | supported
40168 | ClcTotVA |  |  | unimplemented | RW
|  |  | VECTOR | supported
|  |  | ARITHMETIC | supported
40169 | MaxRmpRte |  |  | unimplemented | RW
40170 | ECPNomHz |  |  | unimplemented | RW
40171 | ConnPh |  |  | unimplemented | RW
|  |  | A | supported
|  |  | B | supported
|  |  | C | supported
40172 | WMax_SF |  |  | 1 | R
40173 | VRef_SF |  |  | unimplemented | R
40174 | VRefOfs_SF |  |  | unimplemented | R
40175 | VMinMax_SF |  |  | unimplemented | R
40176 | VAMax_SF |  |  | 1 | R
40177 | VArMax_SF |  |  | 1 | R
40178 | WGra_SF |  |  | -1 | R
40179 | PFMin_SF |  |  | -4 | R
40180 | MaxRmpRte_SF |  |  | unimplemented | R
40181 | ECPNomHz_SF |  |  | unimplemented | R

## 122
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40182 | ID |  |  | 122
40183 | L |  |  | 44
40184 | PVConn |  |  | supported | R
|  |  | CONNECTED | supported
|  |  | AVAILABLE | unimplemented
|  |  | OPERATING | unimplemented
|  |  | TEST | unimplemented
40185 | StorConn |  |  | supported | R
|  |  | CONNECTED | unimplemented
|  |  | AVAILABLE | unimplemented
|  |  | OPERATING | unimplemented
|  |  | TEST | unimplemented
40186 | ECPConn |  |  | supported | R
|  |  | CONNECTED | supported
40187 | ActWh |  |  | supported | R
40191 | ActVAh |  |  | supported | R
40195 | ActVArhQ1 |  |  | unimplemented | R
40199 | ActVArhQ2 |  |  | unimplemented | R
40203 | ActVArhQ3 |  |  | unimplemented | R
40207 | ActVArhQ4 |  |  | unimplemented | R
40211 | VArAval |  |  | unimplemented | R
40212 | VArAval_SF |  |  | unimplemented | R
40213 | WAval |  |  | unimplemented | R
40214 | WAval_SF |  |  | unimplemented | R
40215 | StSetLimMsk |  |  | supported | R
|  |  | WMax | supported
|  |  | VAMax | supported
|  |  | VArAval | unimplemented
|  |  | VArMaxQ1 | supported |  | Since reactive power operates with the same limit on all quadrants, bits VArMaxQ1, VArMaxQ2, VArMaxQ3, VArMaxQ4 are set together.
|  |  | VArMaxQ2 | supported |  | Since reactive power operates with the same limit on all quadrants, bits VArMaxQ1, VArMaxQ2, VArMaxQ3, VArMaxQ4 are set together.
|  |  | VArMaxQ3 | supported |  | Since reactive power operates with the same limit on all quadrants, bits VArMaxQ1, VArMaxQ2, VArMaxQ3, VArMaxQ4 are set together.
|  |  | VArMaxQ4 | supported |  | Since reactive power operates with the same limit on all quadrants, bits VArMaxQ1, VArMaxQ2, VArMaxQ3, VArMaxQ4 are set together.
|  |  | PFMinQ1 | unimplemented
|  |  | PFMinQ2 | unimplemented
|  |  | PFMinQ3 | unimplemented
|  |  | PFMinQ4 | unimplemented
40217 | StActCtl |  |  | supported | R
|  |  | FixedW | supported
|  |  | FixedVAR | supported
|  |  | FixedPF | supported
|  |  | Volt-VAr | unimplemented
|  |  | Freq-Watt-Param | unimplemented
|  |  | Freq-Watt-Curve | unimplemented
|  |  | Dyn-Reactive-Current | unimplemented
|  |  | LVRT | unimplemented
|  |  | HVRT | unimplemented
|  |  | Watt-PF | unimplemented
|  |  | Volt-Watt | unimplemented
|  |  | Scheduled | unimplemented
|  |  | LFRT | unimplemented
|  |  | HFRT | unimplemented
40219 | TmSrc |  |  | unimplemented | R
40223 | Tms |  |  | supported | R
40225 | RtSt |  |  | supported | R
|  |  | LVRT_ACTIVE | supported
|  |  | HVRT_ACTIVE | supported
|  |  | LFRT_ACTIVE | supported
|  |  | HFRT_ACTIVE | supported
40226 | Ris |  |  | supported | R
40227 | Ris_SF |  |  | 3 | R

## 123
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40228 | ID |  |  | 123
40229 | L |  |  | 24
40230 | Conn_WinTms |  |  | supported | RW
40231 | Conn_RvrtTms |  |  | supported | RW
40232 | Conn |  |  | supported | RW
|  |  | DISCONNECT | supported
|  |  | CONNECT | supported
40233 | WMaxLimPct |  |  | supported | RW
40234 | WMaxLimPct_WinTms |  |  | supported | RW
40235 | WMaxLimPct_RvrtTms |  |  | supported | RW | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the control settings will be saved on non-volatile storage and so the user application should not send frequent commands using RvrtTms = 0 because this can damage the memory support.
40236 | WMaxLimPct_RmpTms |  |  | supported | RW
40237 | WMaxLim_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40238 | OutPFSet |  |  | supported | RW
40239 | OutPFSet_WinTms |  |  | supported | RW
40240 | OutPFSet_RvrtTms |  |  | supported | RW | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application should not send frequent commands using RvrtTms = 0 because this can damage the memory support. In case RvtTms > 0 is sent, "default" settings will be restored when reversion time is expired.
40241 | OutPFSet_RmpTms |  |  | supported | RW
40242 | OutPFSet_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40243 | VArWMaxPct |  |  | supported | RW
40244 | VArMaxPct |  |  | supported | RW
40245 | VArAvalPct |  |  | unimplemented | RW
40246 | VArPct_WinTms |  |  | supported | RW
40247 | VArPct_RvrtTms |  |  | supported | RW | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application should not send frequent commands using RvrtTms = 0 because this can damage the memory support. In case RvtTms > 0 is sent, "default" settings will be restored when reversion time is expired.
40248 | VArPct_RmpTms |  |  | supported | RW
40249 | VArPct_Mod |  |  | supported | RW
|  |  | NONE | unimplemented
|  |  | WMax | supported
|  |  | VArMax | supported
|  |  | VArAval | unimplemented
40250 | VArPct_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40251 | WMaxLimPct_SF |  |  | -1 | R
40252 | OutPFSet_SF |  |  | -4 | R
40253 | VArPct_SF |  |  | -1 | R

## 126
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40254 | ID |  |  | 126 |  | Monotony of curve: X values (Vn) for Volt-VAR curve must be arranged in a monotonic increasing sequence.
40255 | L |  |  | 226
40256 | ActCrv |  |  | supported | RW
40257 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40258 | WinTms |  |  | supported | RW | WinTms is placed in subsequent address respect to ModEna register. If WinTms is written after having written 1 on ModEna for enabling the control, the new WinTms value is not applied (because the WinTms setting is acquired immediately when control is enabled). This means that the client application must write the desired time on WinTms register before writing 1 on ModEna for enabling the control.
40259 | RvrtTms |  |  | unimplemented | RW
40260 | RmpTms |  |  | unimplemented | RW
40261 | NCrv |  |  | supported | R
40262 | NPt |  |  | supported | R
40263 | V_SF |  |  | -1 | R
40264 | DeptRef_SF |  |  | -1 | R
40265 | RmpIncDec_SF |  |  | 0 | R
40266 | ActPt | 1 |  | supported | RW
40267 | DeptRef | 1 |  | supported | RW
|  |  | WMax | supported
|  |  | VArMax | supported
|  |  | VArAval | unimplemented
40268 | V1 | 1 |  | supported | RW
40269 | VAr1 | 1 |  | supported | RW
40270 | V2 | 1 |  | supported | RW
40271 | VAr2 | 1 |  | supported | RW
40272 | V3 | 1 |  | supported | RW
40273 | VAr3 | 1 |  | supported | RW
40274 | V4 | 1 |  | supported | RW
40275 | VAr4 | 1 |  | supported | RW
40276 | V5 | 1 |  | supported | RW
40277 | VAr5 | 1 |  | supported | RW
40278 | V6 | 1 |  | supported | RW
40279 | VAr6 | 1 |  | supported | RW
40280 | V7 | 1 |  | supported | RW
40281 | VAr7 | 1 |  | supported | RW
40282 | V8 | 1 |  | supported | RW
40283 | VAr8 | 1 |  | supported | RW
40284 | V9 | 1 |  | supported | RW
40285 | VAr9 | 1 |  | supported | RW
40286 | V10 | 1 |  | supported | RW
40287 | VAr10 | 1 |  | supported | RW
40288 | V11 | 1 |  | unimplemented | RW
40289 | VAr11 | 1 |  | unimplemented | RW
40290 | V12 | 1 |  | unimplemented | RW
40291 | VAr12 | 1 |  | unimplemented | RW
40292 | V13 | 1 |  | unimplemented | RW
40293 | VAr13 | 1 |  | unimplemented | RW
40294 | V14 | 1 |  | unimplemented | RW
40295 | VAr14 | 1 |  | unimplemented | RW
40296 | V15 | 1 |  | unimplemented | RW
40297 | VAr15 | 1 |  | unimplemented | RW
40298 | V16 | 1 |  | unimplemented | RW
40299 | VAr16 | 1 |  | unimplemented | RW
40300 | V17 | 1 |  | unimplemented | RW
40301 | VAr17 | 1 |  | unimplemented | RW
40302 | V18 | 1 |  | unimplemented | RW
40303 | VAr18 | 1 |  | unimplemented | RW
40304 | V19 | 1 |  | unimplemented | RW
40305 | VAr19 | 1 |  | unimplemented | RW
40306 | V20 | 1 |  | unimplemented | RW
40307 | VAr20 | 1 |  | unimplemented | RW
40308 | CrvNam | 1 |  | supported | RW
40316 | RmpTms | 1 |  | unimplemented | RW
40317 | RmpDecTmm | 1 |  | unimplemented | RW
40318 | RmpIncTmm | 1 |  | unimplemented | RW
40319 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | unimplemented
40320 | ActPt | 2 |  | supported | RW
40321 | DeptRef | 2 |  | supported | RW
40322 | V1 | 2 |  | supported | RW
40323 | VAr1 | 2 |  | supported | RW
40324 | V2 | 2 |  | supported | RW
40325 | VAr2 | 2 |  | supported | RW
40326 | V3 | 2 |  | supported | RW
40327 | VAr3 | 2 |  | supported | RW
40328 | V4 | 2 |  | supported | RW
40329 | VAr4 | 2 |  | supported | RW
40330 | V5 | 2 |  | supported | RW
40331 | VAr5 | 2 |  | supported | RW
40332 | V6 | 2 |  | supported | RW
40333 | VAr6 | 2 |  | supported | RW
40334 | V7 | 2 |  | supported | RW
40335 | VAr7 | 2 |  | supported | RW
40336 | V8 | 2 |  | supported | RW
40337 | VAr8 | 2 |  | supported | RW
40338 | V9 | 2 |  | supported | RW
40339 | VAr9 | 2 |  | supported | RW
40340 | V10 | 2 |  | supported | RW
40341 | VAr10 | 2 |  | supported | RW
40342 | V11 | 2 |  | unimplemented | RW
40343 | VAr11 | 2 |  | unimplemented | RW
40344 | V12 | 2 |  | unimplemented | RW
40345 | VAr12 | 2 |  | unimplemented | RW
40346 | V13 | 2 |  | unimplemented | RW
40347 | VAr13 | 2 |  | unimplemented | RW
40348 | V14 | 2 |  | unimplemented | RW
40349 | VAr14 | 2 |  | unimplemented | RW
40350 | V15 | 2 |  | unimplemented | RW
40351 | VAr15 | 2 |  | unimplemented | RW
40352 | V16 | 2 |  | unimplemented | RW
40353 | VAr16 | 2 |  | unimplemented | RW
40354 | V17 | 2 |  | unimplemented | RW
40355 | VAr17 | 2 |  | unimplemented | RW
40356 | V18 | 2 |  | unimplemented | RW
40357 | VAr18 | 2 |  | unimplemented | RW
40358 | V19 | 2 |  | unimplemented | RW
40359 | VAr19 | 2 |  | unimplemented | RW
40360 | V20 | 2 |  | unimplemented | RW
40361 | VAr20 | 2 |  | unimplemented | RW
40362 | CrvNam | 2 |  | supported | RW
40370 | RmpTms | 2 |  | unimplemented | RW
40371 | RmpDecTmm | 2 |  | unimplemented | RW
40372 | RmpIncTmm | 2 |  | unimplemented | RW
40373 | ReadOnly | 2 |  | supported | R
40374 | ActPt | 3 |  | supported | RW
40375 | DeptRef | 3 |  | supported | RW
40376 | V1 | 3 |  | supported | RW
40377 | VAr1 | 3 |  | supported | RW
40378 | V2 | 3 |  | supported | RW
40379 | VAr2 | 3 |  | supported | RW
40380 | V3 | 3 |  | supported | RW
40381 | VAr3 | 3 |  | supported | RW
40382 | V4 | 3 |  | supported | RW
40383 | VAr4 | 3 |  | supported | RW
40384 | V5 | 3 |  | supported | RW
40385 | VAr5 | 3 |  | supported | RW
40386 | V6 | 3 |  | supported | RW
40387 | VAr6 | 3 |  | supported | RW
40388 | V7 | 3 |  | supported | RW
40389 | VAr7 | 3 |  | supported | RW
40390 | V8 | 3 |  | supported | RW
40391 | VAr8 | 3 |  | supported | RW
40392 | V9 | 3 |  | supported | RW
40393 | VAr9 | 3 |  | supported | RW
40394 | V10 | 3 |  | supported | RW
40395 | VAr10 | 3 |  | supported | RW
40396 | V11 | 3 |  | unimplemented | RW
40397 | VAr11 | 3 |  | unimplemented | RW
40398 | V12 | 3 |  | unimplemented | RW
40399 | VAr12 | 3 |  | unimplemented | RW
40400 | V13 | 3 |  | unimplemented | RW
40401 | VAr13 | 3 |  | unimplemented | RW
40402 | V14 | 3 |  | unimplemented | RW
40403 | VAr14 | 3 |  | unimplemented | RW
40404 | V15 | 3 |  | unimplemented | RW
40405 | VAr15 | 3 |  | unimplemented | RW
40406 | V16 | 3 |  | unimplemented | RW
40407 | VAr16 | 3 |  | unimplemented | RW
40408 | V17 | 3 |  | unimplemented | RW
40409 | VAr17 | 3 |  | unimplemented | RW
40410 | V18 | 3 |  | unimplemented | RW
40411 | VAr18 | 3 |  | unimplemented | RW
40412 | V19 | 3 |  | unimplemented | RW
40413 | VAr19 | 3 |  | unimplemented | RW
40414 | V20 | 3 |  | unimplemented | RW
40415 | VAr20 | 3 |  | unimplemented | RW
40416 | CrvNam | 3 |  | supported | RW
40424 | RmpTms | 3 |  | unimplemented | RW
40425 | RmpDecTmm | 3 |  | unimplemented | RW
40426 | RmpIncTmm | 3 |  | unimplemented | RW
40427 | ReadOnly | 3 |  | supported | R
40428 | ActPt | 4 |  | supported | RW
40429 | DeptRef | 4 |  | supported | RW
40430 | V1 | 4 |  | supported | RW
40431 | VAr1 | 4 |  | supported | RW
40432 | V2 | 4 |  | supported | RW
40433 | VAr2 | 4 |  | supported | RW
40434 | V3 | 4 |  | supported | RW
40435 | VAr3 | 4 |  | supported | RW
40436 | V4 | 4 |  | supported | RW
40437 | VAr4 | 4 |  | supported | RW
40438 | V5 | 4 |  | supported | RW
40439 | VAr5 | 4 |  | supported | RW
40440 | V6 | 4 |  | supported | RW
40441 | VAr6 | 4 |  | supported | RW
40442 | V7 | 4 |  | supported | RW
40443 | VAr7 | 4 |  | supported | RW
40444 | V8 | 4 |  | supported | RW
40445 | VAr8 | 4 |  | supported | RW
40446 | V9 | 4 |  | supported | RW
40447 | VAr9 | 4 |  | supported | RW
40448 | V10 | 4 |  | supported | RW
40449 | VAr10 | 4 |  | supported | RW
40450 | V11 | 4 |  | unimplemented | RW
40451 | VAr11 | 4 |  | unimplemented | RW
40452 | V12 | 4 |  | unimplemented | RW
40453 | VAr12 | 4 |  | unimplemented | RW
40454 | V13 | 4 |  | unimplemented | RW
40455 | VAr13 | 4 |  | unimplemented | RW
40456 | V14 | 4 |  | unimplemented | RW
40457 | VAr14 | 4 |  | unimplemented | RW
40458 | V15 | 4 |  | unimplemented | RW
40459 | VAr15 | 4 |  | unimplemented | RW
40460 | V16 | 4 |  | unimplemented | RW
40461 | VAr16 | 4 |  | unimplemented | RW
40462 | V17 | 4 |  | unimplemented | RW
40463 | VAr17 | 4 |  | unimplemented | RW
40464 | V18 | 4 |  | unimplemented | RW
40465 | VAr18 | 4 |  | unimplemented | RW
40466 | V19 | 4 |  | unimplemented | RW
40467 | VAr19 | 4 |  | unimplemented | RW
40468 | V20 | 4 |  | unimplemented | RW
40469 | VAr20 | 4 |  | unimplemented | RW
40470 | CrvNam | 4 |  | supported | RW
40478 | RmpTms | 4 |  | unimplemented | RW
40479 | RmpDecTmm | 4 |  | unimplemented | RW
40480 | RmpIncTmm | 4 |  | unimplemented | RW
40481 | ReadOnly | 4 |  | supported | R

## 127
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40482 | ID |  |  | 127
40483 | L |  |  | 10
40484 | WGra |  |  | supported | RW
40485 | HzStr |  |  | supported | RW
40486 | HzStop |  |  | supported | RW
40487 | HysEna |  |  | supported | RW
|  |  | ENABLED | supported
40488 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40489 | HzStopWGra |  |  | supported | RW
40490 | WGra_SF |  |  | 0 | R
40491 | HzStrStop_SF |  |  | -2 | R
40492 | RmpIncDec_SF |  |  | 0 | R
40493 | Pad |  |  |  | R

## 129
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40494 | ID |  |  | 129
40495 | L |  |  | 60
40496 | ActCrv |  |  | supported | RW
40497 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40498 | WinTms |  |  | unimplemented | RW
40499 | RvrtTms |  |  | unimplemented | RW
40500 | RmpTms |  |  | unimplemented | RW
40501 | NCrv |  |  | supported | R
40502 | NPt |  |  | supported | R
40503 | Tms_SF |  |  | -2 | R
40504 | V_SF |  |  | -1 | R
40505 | Pad |  |  |  | R
40506 | ActPt | 1 |  | supported | RW
40507 | Tms1 | 1 |  | supported | RW
40508 | V1 | 1 |  | supported | RW
40509 | Tms2 | 1 |  | supported | RW
40510 | V2 | 1 |  | supported | RW
40511 | Tms3 | 1 |  | supported | RW
40512 | V3 | 1 |  | supported | RW
40513 | Tms4 | 1 |  | supported | RW
40514 | V4 | 1 |  | supported | RW
40515 | Tms5 | 1 |  | supported | RW
40516 | V5 | 1 |  | supported | RW
40517 | Tms6 | 1 |  | supported | RW
40518 | V6 | 1 |  | supported | RW
40519 | Tms7 | 1 |  | unimplemented | RW
40520 | V7 | 1 |  | unimplemented | RW
40521 | Tms8 | 1 |  | unimplemented | RW
40522 | V8 | 1 |  | unimplemented | RW
40523 | Tms9 | 1 |  | unimplemented | RW
40524 | V9 | 1 |  | unimplemented | RW
40525 | Tms10 | 1 |  | unimplemented | RW
40526 | V10 | 1 |  | unimplemented | RW
40527 | Tms11 | 1 |  | unimplemented | RW
40528 | V11 | 1 |  | unimplemented | RW
40529 | Tms12 | 1 |  | unimplemented | RW
40530 | V12 | 1 |  | unimplemented | RW
40531 | Tms13 | 1 |  | unimplemented | RW
40532 | V13 | 1 |  | unimplemented | RW
40533 | Tms14 | 1 |  | unimplemented | RW
40534 | V14 | 1 |  | unimplemented | RW
40535 | Tms15 | 1 |  | unimplemented | RW
40536 | V15 | 1 |  | unimplemented | RW
40537 | Tms16 | 1 |  | unimplemented | RW
40538 | V16 | 1 |  | unimplemented | RW
40539 | Tms17 | 1 |  | unimplemented | RW
40540 | V17 | 1 |  | unimplemented | RW
40541 | Tms18 | 1 |  | unimplemented | RW
40542 | V18 | 1 |  | unimplemented | RW
40543 | Tms19 | 1 |  | unimplemented | RW
40544 | V19 | 1 |  | unimplemented | RW
40545 | Tms20 | 1 |  | unimplemented | RW
40546 | V20 | 1 |  | unimplemented | RW
40547 | CrvNam | 1 |  | supported | RW
40555 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | unimplemented

## 130
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40556 | ID |  |  | 130
40557 | L |  |  | 60
40558 | ActCrv |  |  | supported | RW
40559 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40560 | WinTms |  |  | unimplemented | RW
40561 | RvrtTms |  |  | unimplemented | RW
40562 | RmpTms |  |  | unimplemented | RW
40563 | NCrv |  |  | supported | R
40564 | NPt |  |  | supported | R
40565 | Tms_SF |  |  | -2 | R
40566 | V_SF |  |  | -1 | R
40567 | Pad |  |  |  | R
40568 | ActPt | 1 |  | supported | RW
40569 | Tms1 | 1 |  | supported | RW
40570 | V1 | 1 |  | supported | RW
40571 | Tms2 | 1 |  | supported | RW
40572 | V2 | 1 |  | supported | RW
40573 | Tms3 | 1 |  | supported | RW
40574 | V3 | 1 |  | supported | RW
40575 | Tms4 | 1 |  | supported | RW
40576 | V4 | 1 |  | supported | RW
40577 | Tms5 | 1 |  | supported | RW
40578 | V5 | 1 |  | supported | RW
40579 | Tms6 | 1 |  | supported | RW
40580 | V6 | 1 |  | supported | RW
40581 | Tms7 | 1 |  | unimplemented | RW
40582 | V7 | 1 |  | unimplemented | RW
40583 | Tms8 | 1 |  | unimplemented | RW
40584 | V8 | 1 |  | unimplemented | RW
40585 | Tms9 | 1 |  | unimplemented | RW
40586 | V9 | 1 |  | unimplemented | RW
40587 | Tms10 | 1 |  | unimplemented | RW
40588 | V10 | 1 |  | unimplemented | RW
40589 | Tms11 | 1 |  | unimplemented | RW
40590 | V11 | 1 |  | unimplemented | RW
40591 | Tms12 | 1 |  | unimplemented | RW
40592 | V12 | 1 |  | unimplemented | RW
40593 | Tms13 | 1 |  | unimplemented | RW
40594 | V13 | 1 |  | unimplemented | RW
40595 | Tms14 | 1 |  | unimplemented | RW
40596 | V14 | 1 |  | unimplemented | RW
40597 | Tms15 | 1 |  | unimplemented | RW
40598 | V15 | 1 |  | unimplemented | RW
40599 | Tms16 | 1 |  | unimplemented | RW
40600 | V16 | 1 |  | unimplemented | RW
40601 | Tms17 | 1 |  | unimplemented | RW
40602 | V17 | 1 |  | unimplemented | RW
40603 | Tms18 | 1 |  | unimplemented | RW
40604 | V18 | 1 |  | unimplemented | RW
40605 | Tms19 | 1 |  | unimplemented | RW
40606 | V19 | 1 |  | unimplemented | RW
40607 | Tms20 | 1 |  | unimplemented | RW
40608 | V20 | 1 |  | unimplemented | RW
40609 | CrvNam | 1 |  | supported | RW
40617 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | unimplemented

## 132
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40618 | ID |  |  | 132 |  | Monotony of curve: X values (Vn) for Volt-Watt curve must be arranged in a monotonic increasing sequence.
40619 | L |  |  | 226
40620 | ActCrv |  |  | supported | RW
40621 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40622 | WinTms |  |  | supported | RW | WinTms is placed in subsequent address respect to ModEna register. If WinTms is written after having written 1 on ModEna for enabling the control, the new WinTms value is not applied (because the WinTms setting is acquired immediately when control is enabled). This means that the client application must write the desired time on WinTms register before writing 1 on ModEna for enabling the control.
40623 | RvrtTms |  |  | unimplemented | RW
40624 | RmpTms |  |  | unimplemented | RW
40625 | NCrv |  |  | supported | R
40626 | NPt |  |  | supported | R
40627 | V_SF |  |  | -1 | R
40628 | DeptRef_SF |  |  | -1 | R
40629 | RmpIncDec_SF |  |  | 0 | R
40630 | ActPt | 1 |  | supported | RW
40631 | DeptRef | 1 |  | supported | RW
|  |  | %WMax | supported
|  |  | %WAval | supported
40632 | V1 | 1 |  | supported | RW
40633 | W1 | 1 |  | supported | RW
40634 | V2 | 1 |  | supported | RW
40635 | W2 | 1 |  | supported | RW
40636 | V3 | 1 |  | supported | RW
40637 | W3 | 1 |  | supported | RW
40638 | V4 | 1 |  | supported | RW
40639 | W4 | 1 |  | supported | RW
40640 | V5 | 1 |  | supported | RW
40641 | W5 | 1 |  | supported | RW
40642 | V6 | 1 |  | supported | RW
40643 | W6 | 1 |  | supported | RW
40644 | V7 | 1 |  | supported | RW
40645 | W7 | 1 |  | supported | RW
40646 | V8 | 1 |  | supported | RW
40647 | W8 | 1 |  | supported | RW
40648 | V9 | 1 |  | supported | RW
40649 | W9 | 1 |  | supported | RW
40650 | V10 | 1 |  | supported | RW
40651 | W10 | 1 |  | supported | RW
40652 | V11 | 1 |  | unimplemented | RW
40653 | W11 | 1 |  | unimplemented | RW
40654 | V12 | 1 |  | unimplemented | RW
40655 | W12 | 1 |  | unimplemented | RW
40656 | V13 | 1 |  | unimplemented | RW
40657 | W13 | 1 |  | unimplemented | RW
40658 | V14 | 1 |  | unimplemented | RW
40659 | W14 | 1 |  | unimplemented | RW
40660 | V15 | 1 |  | unimplemented | RW
40661 | W15 | 1 |  | unimplemented | RW
40662 | V16 | 1 |  | unimplemented | RW
40663 | W16 | 1 |  | unimplemented | RW
40664 | V17 | 1 |  | unimplemented | RW
40665 | W17 | 1 |  | unimplemented | RW
40666 | V18 | 1 |  | unimplemented | RW
40667 | W18 | 1 |  | unimplemented | RW
40668 | V19 | 1 |  | unimplemented | RW
40669 | W19 | 1 |  | unimplemented | RW
40670 | V20 | 1 |  | unimplemented | RW
40671 | W20 | 1 |  | unimplemented | RW
40672 | CrvNam | 1 |  | supported | RW
40680 | RmpPt1Tms | 1 |  | supported | RW
40681 | RmpDecTmm | 1 |  | supported | RW
40682 | RmpIncTmm | 1 |  | supported | RW
40683 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | unimplemented
40684 | ActPt | 2 |  | supported | RW
40685 | DeptRef | 2 |  | supported | RW
40686 | V1 | 2 |  | supported | RW
40687 | W1 | 2 |  | supported | RW
40688 | V2 | 2 |  | supported | RW
40689 | W2 | 2 |  | supported | RW
40690 | V3 | 2 |  | supported | RW
40691 | W3 | 2 |  | supported | RW
40692 | V4 | 2 |  | supported | RW
40693 | W4 | 2 |  | supported | RW
40694 | V5 | 2 |  | supported | RW
40695 | W5 | 2 |  | supported | RW
40696 | V6 | 2 |  | supported | RW
40697 | W6 | 2 |  | supported | RW
40698 | V7 | 2 |  | supported | RW
40699 | W7 | 2 |  | supported | RW
40700 | V8 | 2 |  | supported | RW
40701 | W8 | 2 |  | supported | RW
40702 | V9 | 2 |  | supported | RW
40703 | W9 | 2 |  | supported | RW
40704 | V10 | 2 |  | supported | RW
40705 | W10 | 2 |  | supported | RW
40706 | V11 | 2 |  | unimplemented | RW
40707 | W11 | 2 |  | unimplemented | RW
40708 | V12 | 2 |  | unimplemented | RW
40709 | W12 | 2 |  | unimplemented | RW
40710 | V13 | 2 |  | unimplemented | RW
40711 | W13 | 2 |  | unimplemented | RW
40712 | V14 | 2 |  | unimplemented | RW
40713 | W14 | 2 |  | unimplemented | RW
40714 | V15 | 2 |  | unimplemented | RW
40715 | W15 | 2 |  | unimplemented | RW
40716 | V16 | 2 |  | unimplemented | RW
40717 | W16 | 2 |  | unimplemented | RW
40718 | V17 | 2 |  | unimplemented | RW
40719 | W17 | 2 |  | unimplemented | RW
40720 | V18 | 2 |  | unimplemented | RW
40721 | W18 | 2 |  | unimplemented | RW
40722 | V19 | 2 |  | unimplemented | RW
40723 | W19 | 2 |  | unimplemented | RW
40724 | V20 | 2 |  | unimplemented | RW
40725 | W20 | 2 |  | unimplemented | RW
40726 | CrvNam | 2 |  | supported | RW
40734 | RmpPt1Tms | 2 |  | supported | RW
40735 | RmpDecTmm | 2 |  | supported | RW
40736 | RmpIncTmm | 2 |  | supported | RW
40737 | ReadOnly | 2 |  | supported | R
40738 | ActPt | 3 |  | supported | RW
40739 | DeptRef | 3 |  | supported | RW
40740 | V1 | 3 |  | supported | RW
40741 | W1 | 3 |  | supported | RW
40742 | V2 | 3 |  | supported | RW
40743 | W2 | 3 |  | supported | RW
40744 | V3 | 3 |  | supported | RW
40745 | W3 | 3 |  | supported | RW
40746 | V4 | 3 |  | supported | RW
40747 | W4 | 3 |  | supported | RW
40748 | V5 | 3 |  | supported | RW
40749 | W5 | 3 |  | supported | RW
40750 | V6 | 3 |  | supported | RW
40751 | W6 | 3 |  | supported | RW
40752 | V7 | 3 |  | supported | RW
40753 | W7 | 3 |  | supported | RW
40754 | V8 | 3 |  | supported | RW
40755 | W8 | 3 |  | supported | RW
40756 | V9 | 3 |  | supported | RW
40757 | W9 | 3 |  | supported | RW
40758 | V10 | 3 |  | supported | RW
40759 | W10 | 3 |  | supported | RW
40760 | V11 | 3 |  | unimplemented | RW
40761 | W11 | 3 |  | unimplemented | RW
40762 | V12 | 3 |  | unimplemented | RW
40763 | W12 | 3 |  | unimplemented | RW
40764 | V13 | 3 |  | unimplemented | RW
40765 | W13 | 3 |  | unimplemented | RW
40766 | V14 | 3 |  | unimplemented | RW
40767 | W14 | 3 |  | unimplemented | RW
40768 | V15 | 3 |  | unimplemented | RW
40769 | W15 | 3 |  | unimplemented | RW
40770 | V16 | 3 |  | unimplemented | RW
40771 | W16 | 3 |  | unimplemented | RW
40772 | V17 | 3 |  | unimplemented | RW
40773 | W17 | 3 |  | unimplemented | RW
40774 | V18 | 3 |  | unimplemented | RW
40775 | W18 | 3 |  | unimplemented | RW
40776 | V19 | 3 |  | unimplemented | RW
40777 | W19 | 3 |  | unimplemented | RW
40778 | V20 | 3 |  | unimplemented | RW
40779 | W20 | 3 |  | unimplemented | RW
40780 | CrvNam | 3 |  | supported | RW
40788 | RmpPt1Tms | 3 |  | supported | RW
40789 | RmpDecTmm | 3 |  | supported | RW
40790 | RmpIncTmm | 3 |  | supported | RW
40791 | ReadOnly | 3 |  | supported | R
40792 | ActPt | 4 |  | supported | RW
40793 | DeptRef | 4 |  | supported | RW
40794 | V1 | 4 |  | supported | RW
40795 | W1 | 4 |  | supported | RW
40796 | V2 | 4 |  | supported | RW
40797 | W2 | 4 |  | supported | RW
40798 | V3 | 4 |  | supported | RW
40799 | W3 | 4 |  | supported | RW
40800 | V4 | 4 |  | supported | RW
40801 | W4 | 4 |  | supported | RW
40802 | V5 | 4 |  | supported | RW
40803 | W5 | 4 |  | supported | RW
40804 | V6 | 4 |  | supported | RW
40805 | W6 | 4 |  | supported | RW
40806 | V7 | 4 |  | supported | RW
40807 | W7 | 4 |  | supported | RW
40808 | V8 | 4 |  | supported | RW
40809 | W8 | 4 |  | supported | RW
40810 | V9 | 4 |  | supported | RW
40811 | W9 | 4 |  | supported | RW
40812 | V10 | 4 |  | supported | RW
40813 | W10 | 4 |  | supported | RW
40814 | V11 | 4 |  | unimplemented | RW
40815 | W11 | 4 |  | unimplemented | RW
40816 | V12 | 4 |  | unimplemented | RW
40817 | W12 | 4 |  | unimplemented | RW
40818 | V13 | 4 |  | unimplemented | RW
40819 | W13 | 4 |  | unimplemented | RW
40820 | V14 | 4 |  | unimplemented | RW
40821 | W14 | 4 |  | unimplemented | RW
40822 | V15 | 4 |  | unimplemented | RW
40823 | W15 | 4 |  | unimplemented | RW
40824 | V16 | 4 |  | unimplemented | RW
40825 | W16 | 4 |  | unimplemented | RW
40826 | V17 | 4 |  | unimplemented | RW
40827 | W17 | 4 |  | unimplemented | RW
40828 | V18 | 4 |  | unimplemented | RW
40829 | W18 | 4 |  | unimplemented | RW
40830 | V19 | 4 |  | unimplemented | RW
40831 | W19 | 4 |  | unimplemented | RW
40832 | V20 | 4 |  | unimplemented | RW
40833 | W20 | 4 |  | unimplemented | RW
40834 | CrvNam | 4 |  | supported | RW
40842 | RmpPt1Tms | 4 |  | supported | RW
40843 | RmpDecTmm | 4 |  | supported | RW
40844 | RmpIncTmm | 4 |  | supported | RW
40845 | ReadOnly | 4 |  | supported | R

## 135
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40846 | ID |  |  | 135
40847 | L |  |  | 60
40848 | ActCrv |  |  | supported | RW
40849 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40850 | WinTms |  |  | unimplemented | RW
40851 | RvrtTms |  |  | unimplemented | RW
40852 | RmpTms |  |  | unimplemented | RW
40853 | NCrv |  |  | supported | R
40854 | NPt |  |  | supported | R
40855 | Tms_SF |  |  | -2 | R
40856 | Hz_SF |  |  | -2 | R
40857 | Pad |  |  |  | R
40858 | ActPt | 1 |  | supported | RW
40859 | Tms1 | 1 |  | supported | RW
40860 | Hz1 | 1 |  | supported | RW
40861 | Tms2 | 1 |  | supported | RW
40862 | Hz2 | 1 |  | supported | RW
40863 | Tms3 | 1 |  | supported | RW
40864 | Hz3 | 1 |  | supported | RW
40865 | Tms4 | 1 |  | supported | RW
40866 | Hz4 | 1 |  | supported | RW
40867 | Tms5 | 1 |  | supported | RW
40868 | Hz5 | 1 |  | supported | RW
40869 | Tms6 | 1 |  | supported | RW
40870 | Hz6 | 1 |  | supported | RW
40871 | Tms7 | 1 |  | unimplemented | RW
40872 | Hz7 | 1 |  | unimplemented | RW
40873 | Tms8 | 1 |  | unimplemented | RW
40874 | Hz8 | 1 |  | unimplemented | RW
40875 | Tms9 | 1 |  | unimplemented | RW
40876 | Hz9 | 1 |  | unimplemented | RW
40877 | Tms10 | 1 |  | unimplemented | RW
40878 | Hz10 | 1 |  | unimplemented | RW
40879 | Tms11 | 1 |  | unimplemented | RW
40880 | Hz11 | 1 |  | unimplemented | RW
40881 | Tms12 | 1 |  | unimplemented | RW
40882 | Hz12 | 1 |  | unimplemented | RW
40883 | Tms13 | 1 |  | unimplemented | RW
40884 | Hz13 | 1 |  | unimplemented | RW
40885 | Tms14 | 1 |  | unimplemented | RW
40886 | Hz14 | 1 |  | unimplemented | RW
40887 | Tms15 | 1 |  | unimplemented | RW
40888 | Hz15 | 1 |  | unimplemented | RW
40889 | Tms16 | 1 |  | unimplemented | RW
40890 | Hz16 | 1 |  | unimplemented | RW
40891 | Tms17 | 1 |  | unimplemented | RW
40892 | Hz17 | 1 |  | unimplemented | RW
40893 | Tms18 | 1 |  | unimplemented | RW
40894 | Hz18 | 1 |  | unimplemented | RW
40895 | Tms19 | 1 |  | unimplemented | RW
40896 | Hz19 | 1 |  | unimplemented | RW
40897 | Tms20 | 1 |  | unimplemented | RW
40898 | Hz20 | 1 |  | unimplemented | RW
40899 | CrvNam | 1 |  | supported | RW
40907 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | unimplemented

## 136
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40908 | ID |  |  | 136
40909 | L |  |  | 60
40910 | ActCrv |  |  | supported | RW
40911 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40912 | WinTms |  |  | unimplemented | RW
40913 | RvrtTms |  |  | unimplemented | RW
40914 | RmpTms |  |  | unimplemented | RW
40915 | NCrv |  |  | supported | R
40916 | NPt |  |  | supported | R
40917 | Tms_SF |  |  | -2 | R
40918 | Hz_SF |  |  | -2 | R
40919 | Pad |  |  |  | R
40920 | ActPt | 1 |  | supported | RW
40921 | Tms1 | 1 |  | supported | RW
40922 | Hz1 | 1 |  | supported | RW
40923 | Tms2 | 1 |  | supported | RW
40924 | Hz2 | 1 |  | supported | RW
40925 | Tms3 | 1 |  | supported | RW
40926 | Hz3 | 1 |  | supported | RW
40927 | Tms4 | 1 |  | supported | RW
40928 | Hz4 | 1 |  | supported | RW
40929 | Tms5 | 1 |  | supported | RW
40930 | Hz5 | 1 |  | supported | RW
40931 | Tms6 | 1 |  | supported | RW
40932 | Hz6 | 1 |  | supported | RW
40933 | Tms7 | 1 |  | unimplemented | RW
40934 | Hz7 | 1 |  | unimplemented | RW
40935 | Tms8 | 1 |  | unimplemented | RW
40936 | Hz8 | 1 |  | unimplemented | RW
40937 | Tms9 | 1 |  | unimplemented | RW
40938 | Hz9 | 1 |  | unimplemented | RW
40939 | Tms10 | 1 |  | unimplemented | RW
40940 | Hz10 | 1 |  | unimplemented | RW
40941 | Tms11 | 1 |  | unimplemented | RW
40942 | Hz11 | 1 |  | unimplemented | RW
40943 | Tms12 | 1 |  | unimplemented | RW
40944 | Hz12 | 1 |  | unimplemented | RW
40945 | Tms13 | 1 |  | unimplemented | RW
40946 | Hz13 | 1 |  | unimplemented | RW
40947 | Tms14 | 1 |  | unimplemented | RW
40948 | Hz14 | 1 |  | unimplemented | RW
40949 | Tms15 | 1 |  | unimplemented | RW
40950 | Hz15 | 1 |  | unimplemented | RW
40951 | Tms16 | 1 |  | unimplemented | RW
40952 | Hz16 | 1 |  | unimplemented | RW
40953 | Tms17 | 1 |  | unimplemented | RW
40954 | Hz17 | 1 |  | unimplemented | RW
40955 | Tms18 | 1 |  | unimplemented | RW
40956 | Hz18 | 1 |  | unimplemented | RW
40957 | Tms19 | 1 |  | unimplemented | RW
40958 | Hz19 | 1 |  | unimplemented | RW
40959 | Tms20 | 1 |  | unimplemented | RW
40960 | Hz20 | 1 |  | unimplemented | RW
40961 | CrvNam | 1 |  | supported | RW
40969 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | unimplemented

## 139
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40970 | ID |  |  | 139
40971 | L |  |  | 60
40972 | ActCrv |  |  | supported | RW
40973 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported |  | The enable of LVRT is shared with HVRT so setting this bit has the same effect on "ModEna" register of M140.
40974 | WinTms |  |  | unimplemented | RW
40975 | RvrtTms |  |  | unimplemented | RW
40976 | RmpTms |  |  | unimplemented | RW
40977 | NCrv |  |  | supported | R
40978 | NPt |  |  | supported | R
40979 | Tms_SF |  |  | -2 | R
40980 | V_SF |  |  | -1 | R
40981 | CrvType |  |  | supported | R
|  |  | CEASE_TO_ENERGIZE | supported
40982 | ActPt | 1 |  | supported | RW
40983 | Tms1 | 1 |  | unimplemented | RW
40984 | V1 | 1 |  | supported | RW
40985 | Tms2 | 1 |  | unimplemented | RW
40986 | V2 | 1 |  | unimplemented | RW
40987 | Tms3 | 1 |  | unimplemented | RW
40988 | V3 | 1 |  | unimplemented | RW
40989 | Tms4 | 1 |  | unimplemented | RW
40990 | V4 | 1 |  | unimplemented | RW
40991 | Tms5 | 1 |  | unimplemented | RW
40992 | V5 | 1 |  | unimplemented | RW
40993 | Tms6 | 1 |  | unimplemented | RW
40994 | V6 | 1 |  | unimplemented | RW
40995 | Tms7 | 1 |  | unimplemented | RW
40996 | V7 | 1 |  | unimplemented | RW
40997 | Tms8 | 1 |  | unimplemented | RW
40998 | V8 | 1 |  | unimplemented | RW
40999 | Tms9 | 1 |  | unimplemented | RW
41000 | V9 | 1 |  | unimplemented | RW
41001 | Tms10 | 1 |  | unimplemented | RW
41002 | V10 | 1 |  | unimplemented | RW
41003 | Tms11 | 1 |  | unimplemented | RW
41004 | V11 | 1 |  | unimplemented | RW
41005 | Tms12 | 1 |  | unimplemented | RW
41006 | V12 | 1 |  | unimplemented | RW
41007 | Tms13 | 1 |  | unimplemented | RW
41008 | V13 | 1 |  | unimplemented | RW
41009 | Tms14 | 1 |  | unimplemented | RW
41010 | V14 | 1 |  | unimplemented | RW
41011 | Tms15 | 1 |  | unimplemented | RW
41012 | V15 | 1 |  | unimplemented | RW
41013 | Tms16 | 1 |  | unimplemented | RW
41014 | V16 | 1 |  | unimplemented | RW
41015 | Tms17 | 1 |  | unimplemented | RW
41016 | V17 | 1 |  | unimplemented | RW
41017 | Tms18 | 1 |  | unimplemented | RW
41018 | V18 | 1 |  | unimplemented | RW
41019 | Tms19 | 1 |  | unimplemented | RW
41020 | V19 | 1 |  | unimplemented | RW
41021 | Tms20 | 1 |  | unimplemented | RW
41022 | V20 | 1 |  | unimplemented | RW
41023 | CrvNam | 1 |  | supported | RW
41031 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | unimplemented

## 140
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41032 | ID |  |  | 140
41033 | L |  |  | 60
41034 | ActCrv |  |  | supported | RW
41035 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported |  | The enable of HVRT is shared with LVRT so setting this bit has the same effect on "ModEna" register of M139.
41036 | WinTms |  |  | unimplemented | RW
41037 | RvrtTms |  |  | unimplemented | RW
41038 | RmpTms |  |  | unimplemented | RW
41039 | NCrv |  |  | supported | R
41040 | NPt |  |  | supported | R
41041 | Tms_SF |  |  | -2 | R
41042 | V_SF |  |  | -1 | R
41043 | CrvType |  |  | supported | R
|  |  | CEASE_TO_ENERGIZE | supported
41044 | ActPt | 1 |  | supported | RW
41045 | Tms1 | 1 |  | unimplemented | RW
41046 | V1 | 1 |  | supported | RW
41047 | Tms2 | 1 |  | unimplemented | RW
41048 | V2 | 1 |  | unimplemented | RW
41049 | Tms3 | 1 |  | unimplemented | RW
41050 | V3 | 1 |  | unimplemented | RW
41051 | Tms4 | 1 |  | unimplemented | RW
41052 | V4 | 1 |  | unimplemented | RW
41053 | Tms5 | 1 |  | unimplemented | RW
41054 | V5 | 1 |  | unimplemented | RW
41055 | Tms6 | 1 |  | unimplemented | RW
41056 | V6 | 1 |  | unimplemented | RW
41057 | Tms7 | 1 |  | unimplemented | RW
41058 | V7 | 1 |  | unimplemented | RW
41059 | Tms8 | 1 |  | unimplemented | RW
41060 | V8 | 1 |  | unimplemented | RW
41061 | Tms9 | 1 |  | unimplemented | RW
41062 | V9 | 1 |  | unimplemented | RW
41063 | Tms10 | 1 |  | unimplemented | RW
41064 | V10 | 1 |  | unimplemented | RW
41065 | Tms11 | 1 |  | unimplemented | RW
41066 | V11 | 1 |  | unimplemented | RW
41067 | Tms12 | 1 |  | unimplemented | RW
41068 | V12 | 1 |  | unimplemented | RW
41069 | Tms13 | 1 |  | unimplemented | RW
41070 | V13 | 1 |  | unimplemented | RW
41071 | Tms14 | 1 |  | unimplemented | RW
41072 | V14 | 1 |  | unimplemented | RW
41073 | Tms15 | 1 |  | unimplemented | RW
41074 | V15 | 1 |  | unimplemented | RW
41075 | Tms16 | 1 |  | unimplemented | RW
41076 | V16 | 1 |  | unimplemented | RW
41077 | Tms17 | 1 |  | unimplemented | RW
41078 | V17 | 1 |  | unimplemented | RW
41079 | Tms18 | 1 |  | unimplemented | RW
41080 | V18 | 1 |  | unimplemented | RW
41081 | Tms19 | 1 |  | unimplemented | RW
41082 | V19 | 1 |  | unimplemented | RW
41083 | Tms20 | 1 |  | unimplemented | RW
41084 | V20 | 1 |  | unimplemented | RW
41085 | CrvNam | 1 |  | supported | RW
41093 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | unimplemented

## 145
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41094 | ID |  |  | 145
41095 | L |  |  | 8
41096 | Ramp Up Rate (NomRmpUpRte) |  |  | supported | RW
41097 | NomRmpDnRte |  |  | unimplemented | RW
41098 | Emergency Ramp Up Rate (EmgRmpUpRte) |  |  | unimplemented | RW
41099 | Emergency Ramp Down Rate (EmgRmpDnRte) |  |  | unimplemented | RW
41100 | Connect Ramp Up Rate (ConnRmpUpRte) |  |  | supported | RW
41101 | Connect Ramp Down Rate (ConnRmpDnRte) |  |  | unimplemented | RW
41102 | Default Ramp Rate (AGra) |  |  | unimplemented | RW
41103 | Ramp Rate Scale Factor (Rmp_SF) |  |  | -1 | R

## 160
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41104 | ID |  |  | 160
41105 | L |  |  | 68
41106 | Current Scale Factor (DCA_SF) |  |  | -1 | R
41107 | Voltage Scale Factor (DCV_SF) |  |  | -1 | R
41108 | Power Scale Factor (DCW_SF) |  |  | 1 | R
41109 | Energy Scale Factor (DCWH_SF) |  |  | unimplemented | R
41110 | Global Events (Evt) |  |  | supported | R
|  |  | Ground Fault (GROUND_FAULT) | supported |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
|  |  | Input Over Voltage (INPUT_OVER_VOLTAGE) | supported |  | This state corresponds to the following internal alarms: - E002: Input OV
|  |  | Reserved (RESERVED) | unimplemented
|  |  | DC Disconnect (DC_DISCONNECT) | unimplemented
|  |  | Cabinet Open (CABINET_OPEN) | unimplemented
|  |  | Manual Shutdown (MANUAL_SHUTDOWN) | supported |  | This state corresponds to the following internal alarms: - E035: Remote off
|  |  | Over Temperature (OVER_TEMP) | supported |  | This state corresponds to the following internal alarms: - E014: OTH
|  |  | Blown Fuse (BLOWN_FUSE) | unimplemented
|  |  | Under Temperature (UNDER_TEMP) | supported |  | This state corresponds to the following internal alarms: - E033: UTH
|  |  | Memory Loss (MEMORY_LOSS) | supported |  | This state corresponds to statistics memory fault.
|  |  | Arc Detection (ARC_DETECTION) | supported |  | This state corresponds to the following internal alarms: - E050: Arc-Fault
|  |  | Test Failed (TEST_FAILED) | supported |  | This state corresponds to the following internal alarms: - E005: Internal bus fault - E013: Wrong DC input mode - E019: Lekage current self-test fault - E020: Grid interface self-test fault - E021: Grid interface self-test fault - E053: Arc-fault detector self-test fault - E078: R-iso self-test fault
|  |  | Under Voltage (INPUT_UNDER_VOLTAGE) | supported |  | This state corresponds to the following internal alarms: - W002: Input UV
|  |  | Over Current (INPUT_OVER_CURRENT) | supported |  | This state corresponds to the following internal alarms: - E001: Input OC
41112 | Number of Modules (N) |  |  | supported | R
41113 | Timestamp Period (TmsPer) |  |  | unimplemented | R
41114 | Input ID (ID) | 1 |  | supported | R
41115 | Input ID Sting (IDStr) | 1 |  | supported | R
41123 | DC Current (DCA) | 1 |  | supported | R
41124 | DC Voltage (DCV) | 1 |  | supported | R
41125 | DC Power (DCW) | 1 |  | supported | R
41126 | Lifetime Energy (DCWH) | 1 |  | unimplemented | R
41128 | Timestamp (Tms) | 1 |  | unimplemented | R
41130 | Temperature (Tmp) | 1 |  | unimplemented | R
41131 | Operating State (DCSt) | 1 |  | supported | R
|  |  | Off (OFF) | supported |  | This state corresponds to unloaded/disconnected DC channel.
|  |  | Sleeping (SLEEPING) | supported |  | This state corresponds to connected DC channel but not ready for starting MPPT (e.g. for low voltage condition).
|  |  | Starting (STARTING) | supported |  | This state corresponds to connected DC channel starting MPPT regulation.
|  |  | MPPT | supported |  | This state corresponds to connected DC channel running MPPT regulation.
|  |  | Throttled (THROTTLED) | supported |  | This state corresponds to connected DC channel with forced MPPT suspension (e,g, for by-pass or power-saving purposes).
|  |  | Shutting Down (SHUTTING_DOWN) | unimplemented
|  |  | Fault (FAULT) | supported |  | This state corresponds to connected DC channel with pending fault (under-voltage, over-voltage, over-current).
|  |  | Standby (STANDBY) | unimplemented
|  |  | Test (TEST) | unimplemented
|  |  | Reserved (RESERVED) | unimplemented
41132 | Module Events (DCEvt) | 1 |  | supported | R
|  |  | Ground Fault (GROUND_FAULT) | supported |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
|  |  | Input Over Voltage (INPUT_OVER_VOLTAGE) | supported |  | This state corresponds to the following internal alarms: - E002: Input OV
|  |  | Reserved (RESERVED) | unimplemented
|  |  | DC Disconnect (DC_DISCONNECT) | unimplemented
|  |  | Cabinet Open (CABINET_OPEN) | unimplemented
|  |  | Manual Shutdown (MANUAL_SHUTDOWN) | supported |  | This state corresponds to the following internal alarms: - E035: Remote off
|  |  | Over Temperature (OVER_TEMP) | supported |  | This state corresponds to the following internal alarms: - E014: OTH
|  |  | Blown Fuse (BLOWN_FUSE) | unimplemented
|  |  | Under Temperature (UNDER_TEMP) | supported |  | This state corresponds to the following internal alarms: - E033: UTH
|  |  | Memory Loss (MEMORY_LOSS) | supported |  | This state corresponds to statistics memory fault.
|  |  | Arc Detection (ARC_DETECTION) | supported |  | This state corresponds to the following internal alarms: - E050: Arc-Fault
|  |  | Test Failed (TEST_FAILED) | supported |  | This state corresponds to the following internal alarms: - E005: Internal bus fault - E013: Wrong DC input mode - E019: Lekage current self-test fault - E020: Grid interface self-test fault - E021: Grid interface self-test fault - E053: Arc-fault detector self-test fault - E078: R-iso self-test fault
|  |  | Under Voltage (INPUT_UNDER_VOLTAGE) | supported |  | This state corresponds to the following internal alarms: - W002: Input UV
|  |  | Over Current (INPUT_OVER_CURRENT) | supported |  | This state corresponds to the following internal alarms: - E001: Input OC
41134 | Input ID (ID) | 2 |  | supported | R
41135 | Input ID Sting (IDStr) | 2 |  | supported | R
41143 | DC Current (DCA) | 2 |  | supported | R
41144 | DC Voltage (DCV) | 2 |  | supported | R
41145 | DC Power (DCW) | 2 |  | supported | R
41146 | Lifetime Energy (DCWH) | 2 |  | unimplemented | R
41148 | Timestamp (Tms) | 2 |  | unimplemented | R
41150 | Temperature (Tmp) | 2 |  | unimplemented | R
41151 | Operating State (DCSt) | 2 |  | supported | R
41152 | Module Events (DCEvt) | 2 |  | supported | R
41154 | Input ID (ID) | 3 |  | supported | R
41155 | Input ID Sting (IDStr) | 3 |  | supported | R
41163 | DC Current (DCA) | 3 |  | supported | R
41164 | DC Voltage (DCV) | 3 |  | supported | R
41165 | DC Power (DCW) | 3 |  | supported | R
41166 | Lifetime Energy (DCWH) | 3 |  | unimplemented | R
41168 | Timestamp (Tms) | 3 |  | unimplemented | R
41170 | Temperature (Tmp) | 3 |  | unimplemented | R
41171 | Operating State (DCSt) | 3 |  | supported | R
41172 | Module Events (DCEvt) | 3 |  | supported | R

## 65230
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41174 | ID |  |  | 65230
41175 | L |  |  | 1
41176 | LatchRest_Ena |  |  | supported | RW