## ABB-P1
Existing inverter model | Revamping - Option 1 | Revamping - Option 2 | NOTES | NOTA2 | Info inverter
PVI-3.0-TL | UNO-DM-PLUS 3.3/3.6 | FIM-HY-3.0-SE-A | - |  | Inverter con 10 anni di garanzia , facile installazione , connessione Wifi | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
PVI-3.6-TL | UNO-DM-PLUS 3/3.6 | FIM-HY-3.6-SE-A | - |  | Inverter con 10 anni di garanzia , facile installazione , connessione Wifi | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
PVI-4.2-TL | UNO-DM-PLUS 4.0/4.6 | FIM-HY-4.0-SE-A FIM-HY-4.6-SE-A | - |  | Inverter con 10 anni di garanzia , facile installazione , connessione Wifi | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
PVI-3.8-I-OUTD |  |  | In caso di PowerUNO, se il cliente ha un parallelo in impianto, deve essere effettuato il parallelo esterno all'inverter (questo non permette il parallelo interno) |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
PVI-4.6-I-OUTD |  |  | In caso di PowerUNO, se il cliente ha un parallelo in impianto, deve essere effettuato il parallelo esterno all'inverter (questo non permette il parallelo interno) |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
PVI-5000-TL | UNO-DM-PLUS 5.0 | FIM-HY-5.0-SE-A | - |  | Inverìter con 10 anni di garanzia , facile installazione , connessione Wifi | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
PVI-6000-TL | UNO-DM-PLUS 6.0 | FIM-HY-6.0-SE-A | - |  | Inverìter con 10 anni di garanzia , facile installazione , connessione Wifi | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
UNO-DM-PLUS 2.0 |  |  | In caso di PowerUNO, se il cliente ha un parallelo in impianto, deve essere effettuato il parallelo esterno all'inverter (questo non permette il parallelo interno) |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
UNO-DM-PLUS 3.0 | - | FIM-HY-3.0-SE-A | - |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
UNO-DM-PLUS 3.3/3.6 | - | FIM-HY-3.6-SE-A | - |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
UNO-DM-PLUS 4.0/4.6 | - | FIM-HY-4.0-SE-A FIM-HY-4.6-SE-A | - |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
UNO-DM-PLUS 5.0 | - | FIM-HY-5.0-SE-A | - |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
UNO-DM-PLUS 6.0 | - | FIM-HY-6.0-SE-A | - |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
FIM-HY-2.0-SE-A | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
FIM-HY-3.0-SE-A | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
FIM-HY-3.3-SE-A | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
FIM-HY-3.6-SE-A | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
FIM-HY-4.0-SE-A | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
FIM-HY-4.6-SE-A | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
FIM-HY-5.0-SE-A | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
FIM-HY-6.0-SE-A | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
Batteria 5KW | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
REACT 1 - 3.6kW | - | FIM-HY-3.6-SE-A | It will be necessary to replace the storage unit and verify whether the available sizes (capacities/ratings) are suitable for the system. |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
REACT 1 - 4.6kW | - | FIM-HY-4.0-SE-A FIM-HY-4.6-SE-A | It will be necessary to replace the storage unit and verify whether the available sizes (capacities/ratings) are suitable for the system. |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
REACT2-UNO-3.6-TL | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
REACT2-UNO-5.0-TL | [5 empty] | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
TRIO-5.8-TL | - | FIM-HY-6.0-SE-A-3PH | - |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
TRIO-7.5-TL | - | FIM-HY-7.5-SE-A-3PH | - |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
TRIO-8.5-TL | - | FIM-HY-8.5-SE-A-3PH | - |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
PVI-6.0-TL | - | FIM-HY-6.0-SE-A-3PH | - |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
PVI-8.0-TL | - | FIM-HY-8.5-SE-A-3PH | - |  |  | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
PVI-10.0-TL | PVS-10-TL | FIM-HY-10-SE-A-3PH | If the customer is working with parallel channels, option 2 is preferable, as option 1 does not support parallel operation. |  | Inverter compatto di ultima generazione, connessione WiFi integrata, file installazione, compatibile con inverter PVI sula linea di comunicazione RS485 | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
PVI-12.5-TL | PVS-12.5-TL | - | If the customer is working with parallel channels, it is necessary to separate the strings, as the inverter does not support parallel operation. |  | Inverter compatto di ultima generazione, connessione WiFi integrata, file installazione, compatibile con inverter PVI sula linea di comunicazione RS486 | Inverter compatto di ultima generazione, connessione WiFi integrata, predisposizione per connessione Batterie
FIM-HY-4.0-SE-A-3PH
FIM-HY-5.0-SE-A-3PH
FIM-HY-6.0-SE-A-3PH
FIM-HY-7.5-SE-A-3PH
FIM-HY-8.0-SE-A-3PH
FIM-HY-8.5-SE-A-3PH
FIM-HY-10-SE-A-3PH
Batteria 5KW
PVS-10 |  |  | Parallelabili
PVS-12,5 |  |  | Parallelabili
PVS-15
TRIO 20 TL - Power Part
TRIO 27 TL - Power Part
TRIO-27.6-TL-WIRING BOX BASE |  |  | Senza sezionatore DC/AC
TRIO-27.6-TL-WIRING BOX S2 |  |  | sezionatore DC/AC
TRIO-27.6-TL-WIRING BOX S2X |  |  | sezionatore DC/AC
TRIO-27.6-TL-WIRING BOX S2F |  |  | sezionatore DC/AC+ Scaricatori
TRIO-27.6-TL-WIRING BOX S1J
TRIO-27.6-TL-WIRING BOX S2J
PRO 33
PVS-20-TL-SX |  |  | TN-S, TN-C, TN-CS,TT
PVS-20-TL-SY |  |  | TN-S, TN-C, TN-CS,TT
PVS-20-TL-SXD |  |  | TN-S, TN-C, TN-CS,TT
PVS-30-TL-SX |  |  | TN-S, TN-C, TN-CS,TT
PVS-30-TL-SY |  |  | TN-S, TN-C, TN-CS,TT
PVS-33-TL-SX |  |  | TN-S, TN-C, TN-CS,TT
PVS-33-TL-SY |  |  | TN-S, TN-C, TN-CS,TT
PVS-33-TL-SI |  |  | TN-S, TN-C, TN-CS,TT,IT
TRIO 50 Power | PVS-50
TRIO 50 DC side
TRIO 50 DC side-S
TRIO 50 DC side-SX
TRIO 50 DC side-SX
TRIO 50 DC side-SY
TRIO 50 AC side
TRIO 50 AC side-S
TRIO 50 AC side-SX
TRIO 50 Power
TRIO 50 TM DC side
TRIO 50 TM DC side-S
TRIO 50 TM DC side-SX
TRIO 50 TM DC side-SX2
TRIO 50 TM AC side
TRIO 50 TM AC side-SX
TRIO 60 Power
TRIO 60 DC side
TRIO 60 DC side-S
TRIO 60 DC side-SX
TRIO 60 DC side-SX
TRI0 60 AC Side
TRIO 60 AC side-S
TRIO 60 AC side-SX
TRIO 60 Power
TRIO 60 TM DC side
TRIO 60 TM DC side-S
TRIO 60 TM DC side-SX
TRIO 60 TM DC side-SX2
TRIO 60 TM AC side
TRIO 60 TM AC side-SX
PVS-50-TL
PVS-50-TL-S
PVS-50-TL-SX
PVS-50-TL-SX2
PVS-60-TL
PVS-60-TL-S
PVS-60-TL-SX
PVS-60-TL-SX2
PVI-STRINGCOMB
TRIO Conjunction Box
PVS-100-TL-POWER MODULE
PVS-100-TL-WIRING BOX
PVS-100-TL-WIRING BOX
PVS-100-TL-WIRING BOX
PVS-100-TL-WIRING BOX
PVS-120-TL-POWER MODULE
PVS-120-TL-WIRING BOX
PVS-120-TL-WIRING BOX
PVS-120-TL-WIRING BOX
PVS-120-TL-WIRING BOX
PVS-175-TL-POWER MODULE
PVS-175-TL-WIRING BOX
PVS-175-TL-WIRING BOX
Drawer 55kW for PVI-PLUS-series
Drawer 67kW for PVI-PLUS-series
Drawer ULTRA

## Santerno
Existing inverter model | Revamping - Option 1 | NOTES | Revamping - Option 2 | NOTES
TG175 - 270 STD | PVR-65 | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution systems: TN and IT (the latter only if the negative pole is grounded). | PVI-165.0-TL | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution system: TN. IT is not supported. 3. Since this is an indoor inverter, it is necessary to verify the available space in the electrical room.
TG175 - 310 STD | PVR-75 PVR-80 | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution systems: TN and IT (the latter only if the negative pole is grounded). | PVI-220.0-TL | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution system: TN. IT is not supported. 3. Since this is an indoor inverter, it is necessary to verify the available space in the electrical room.
TG240 - 270 STD | PVR-65 | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution systems: TN and IT (the latter only if the negative pole is grounded). | PVI-220.0-TL | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution system: TN. IT is not supported. 3. Since this is an indoor inverter, it is necessary to verify the available space in the electrical room.
TG240 - 310 STD | PVR-75 PVR-80 | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution systems: TN and IT (the latter only if the negative pole is grounded). | PVI-220.0-TL | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution system: TN. IT is not supported. 3. Since this is an indoor inverter, it is necessary to verify the available space in the electrical room.
TG300 - 270 STD | PVR-65 | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution systems: TN and IT (the latter only if the negative pole is grounded). | PVI-275.0-TL-IT | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution system: TN. IT is not supported. 3. Since this is an indoor inverter, it is necessary to verify the available space in the electrical room.
TG300 - 310 STD | PVR-75 PVR-80 | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution systems: TN and IT (the latter only if the negative pole is grounded). | PVI-275.0-TL-IT | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution system: TN. IT is not supported. 3. Since this is an indoor inverter, it is necessary to verify the available space in the electrical room.
TG310 - 270 STD | PVR-65 | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution systems: TN and IT (the latter only if the negative pole is grounded). | PVI-275.0-TL-IT | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution system: TN. IT is not supported. 3. Since this is an indoor inverter, it is necessary to verify the available space in the electrical room.
TG310 - 310 STD | PVR-75 PVR-80 | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution systems: TN and IT (the latter only if the negative pole is grounded). | PVI-330.0-TL-IT | 1. In the case of a partial revamping, it is necessary to verify that the newly installed inverters are connected to a secondary circuit separate from the existing inverters. It is not possible to connect in parallel, on the same secondary, inverters of different technologies. 2. Supported distribution system: TN. IT is not supported. 3. Since this is an indoor inverter, it is necessary to verify the available space in the electrical room.

## Danfoss
Existing inverter model | Revamping | NOTES
TLX- 6 kW | FIM-HY-6.0-SE-A-3PH | -
TLX - 8 kW | FIM-HY-8.5-SE-A-3PH | -
TLX -10 kW | PVS-10 FIM-HY-10.0-SE-A-3PH | -
TLX- 12,5 | PVS-12,5
TLX -15 | PVS-15
TLX- 12,5 | PVS-20-TL-SX | -
TLX -15 | PVS-20-TL-SY | -
TLX -15 | PVS-20-TL-SXD | -

## SolarMax
Existing inverter model | Revamping | Modello inverter esistente | Revamping Opzione 1 | Modello inverter esistente | Revamping Opzione 1 | Modello inverter esistente | Revamping Opzione 1 | Modello inverter esistente | Revamping Opzione 1 | NOTE1 | Nota 2 | nfo inverer | NOTES
6SMT | FIM-HY-6.0-SE-A-3PH | 1 - 1 (MPPT1 - MPPT2) | 2 ×20 A | 1000 | 625 | 6,20 Kw | 200 V adj. 200...500 V | 0.7 x Vstart…975 V ( min 145 V ) | 380 V, 400 V Trifase (3 W+PE o 4 W+PE) |  |  |  | -
8SMT | FIM-HY-8.5-SE-A-3PH | 1 - 1 (MPPT1 - MPPT2) | 2 ×20 A | 1000 | 625 | 8,76 Kw | 215 V adj. 215...500 V | 0.7 x Vstart…975 V (min 155 V) | 380 V, 400 V Trifase (3 W+PE o 4 W+PE) |  |  |  | -
10SMT | PVS-10 FIM-HY-10.0-SE-A-3PH | 2 ingressi MC4 per canale | 2 × 17 A | 1100 | 620 | 10.2 kW | 250...500 V (360 V di default) | 460-850 V | 380 V, 400 V Trifase (3 W+PE o 4 W+PE) |  |  |  | -
13SMT | PVS-12,5 | 4 ingressi per 2 MMPT MC4 per canale | 2 × 22 A | 1100 | 620 | 12.76 kW | 250...500 V (360 V di default) | 460-850 V | 380 V, 400 V Trifase (3 W+PE o 4 W+PE)
15SMT | PVS-15 | 4 ingressi per 2 MMPT MC4 per canale | 2 × 22 A | 1100 | 620 | 15.3 kW | 250...500 V (360 V di default) | 460-850 V | 380 V, 400 V Trifase (3 W+PE o 4 W+PE)
13SMT | PVS-20-TL-SX | 4 ingressi per 2 MMPT MC4 per canale | 26A,26A | 1100 | 620 | 20,5 KW | 250...500V (default 430V) | 200…1000 V | TN-S, TN-C, TN-CS, TT000/2 |  |  |  | -
15SMT | PVS-20-TL-SY | 4 ingressi per 2 MMPT MC4 per canale | 26A,26A | 1100 | 620 | 20,5 KW | 250...500V (default 430V) | 200…1000 V | TN-S, TN-C, TN-CS, TT000/2 |  |  |  | -
15SMT | PVS-20-TL-SXD | 8 ingressi per 2 MMPT MC4 per canale | 22A, 26A, 22A, 26A | 1100 | 620 | 20,5 KW | 250...500V (default 430V) | 200…1000 V | TN-S, TN-C, TN-CS, TT |  |  |  | -