## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.4a based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number
Date | 2018-06-05 09:51
Manufacturer Name | FIMER
Product Name | PVS-100/120-TL
Product Models | PVS-120-TL PVS-100-TL PVS-120-TL-B version PVS-100-TL-B version PVS-120-TL-B2 version PVS-100-TL-B2 version
Product Description | Three Phase String Inverter

## Versioning
Version | Change Log | Date of Change | Min. Ref. FW version Inverter | Min. Ref. FW version Q1
0 | - First version - Verified TCP-RTU aligned with ABB SunSpec Server Implementation Guide | 2018-02-08 | 1804E | 0.10.2
1 | - Updated conformance notes for "EvtVnd1" and "EvtVnd2" on M103 - Updated conformance notes for "input-mode" on M160 - Updated conformance notes for writing values on M126 and M132 - Updated conformance notes for Reactive Sign Convention on M103 and M120 | 2018-03-29 | 1804E | 0.10.3
2 | - Added M403 ( String Controller ) | 2018-06-05 | 1814D | 0.10.8
3 | - Included note details | 2019-01-02 | 1814D | 0.10.8
4 | - Included additional comments and fields according to SunSpec reference data model | 2019-10-11 | 1814D | 0.10.8
5 | - Included the vendor specific data model 65232 with additional fuction management | 2021-02-15 | 2040B | 1.0.11
6
7
8
9
10
11
12
13
14
15
16

## 1
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40002 | ID | Common |  | uint16 |  |  | 1 |  |  | All SunSpec compliant devices must include this as the first model
40003 | L |  |  | uint16 |  |  | 66 |  |  | Model Length
40004 | Mn | Manufacturer |  | string |  |  | FIMER |  | R | Well known value registered with SunSpec for compliance
40020 | Md | Model |  | string |  |  | -3P20- |  | R | Manufacturer specific value (32 chars) | Provided Md string is the part number of the specific model: -3P20- = PVS-120-TL -3P80- = PVS-100-TL -3Q14- = PVS-120-TL-B version -3Q15- = PVS-100-TL-B version -3Q41- = PVS-120-TL-B2 version -3Q42- = PVS-100-TL-B2 version
40036 | Opt | Options |  | string |  |  | 0x005C/0x014A/ |  | R | Manufacturer specific value (16 chars) | Provided Opt string is formatted as a list of string fields separated by '/' character [Field 1/Field 2/]: - Field 1: Model identifier formatted as [Model ID + Family ID] where Model ID is the identifier for the inverter type and Family ID is the identifier for the inverter family. The IDs uniquely represent an inverter model. If one of the ID bytes is not-printable then they will be both presented as hexadecimal values preceded by "0x" string; if both ID bytes are printable then they will be presented with the corresponding ASCII characters. IDs pair are: 0x005C for PVS-120-TL (Model ID = 00, Family ID = 5C) 0x045C for PVS-100-TL (Model ID = 04, Family ID = 5C) 0x005C for PVS-120-TL-B version Model ID = 00, Family ID = 5C) 0x045C for PVS-100-TL-B version (Model ID = 04, Family ID = 5C) - Field 2: reserved for internal use
40044 | Vr | Version |  | string |  |  | 1801C |  | R | Manufacturer specific value (16 chars) | Provided SW release version string is formatted as [Y + WY + DW] where Y is the release year (format YY), WY is the release week of the year (format WW) and DW is the release day of the week (encoded as a single ASCII character starting from 'A' which is associated to Monday) Example: 1801C is the encoding number that define the firmware released Wednesday on the first week of 2018
40052 | Number | Serial |  | string |  |  | 001001-3P20-0517 |  | R | Manufacturer specific value (32 chars) | Provided serial number string is formatted as [SN + PN + WY] where SN is the internal serial number of the unit, PN is the internal part number of the unit and WY is the manufacturing week/year date expressed in WWYY format. The inverter label and official serial number is composed by the following format [YW+SN]. Example: the following register value 001001-3P20-0517 is associated as SN=001001; PN = -3P20-; W=05; SN=17. The label serial number is 1705001001.
40068 | Address | Device |  | uint16 |  |  | 1 |  | RW | Modbus device address
40069 | Pad | Pad |  | pad |  |  |  |  | R | Force even alignment

## 103
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40070 | ID | Inverter (Three Phase) |  | uint16 |  |  | 103 |  |  | Include this model for three phase inverter monitoring
40071 | L |  |  | uint16 |  |  | 50 |  |  | Model Length
40072 | A | Amps |  | uint16 | A | A_SF | supported |  | R | AC Current
40073 | AphA | Amps PhaseA |  | uint16 | A | A_SF | supported |  | R | Phase A Current
40074 | AphB | Amps PhaseB |  | uint16 | A | A_SF | supported |  | R | Phase B Current
40075 | AphC | Amps PhaseC |  | uint16 | A | A_SF | supported |  | R | Phase C Current
40076 |  | A_SF |  | sunssf |  |  | -1 |  | R
40077 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | supported |  | R | Phase Voltage AB
40078 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | supported |  | R | Phase Voltage BC
40079 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | supported |  | R | Phase Voltage CA
40080 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | supported |  | R | Phase Voltage AN
40081 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | supported |  | R | Phase Voltage BN
40082 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | supported |  | R | Phase Voltage CN
40083 |  | V_SF |  | sunssf |  |  | -1 |  | R
40084 | W | Watts |  | int16 | W | W_SF | supported |  | R | AC Power
40085 |  | W_SF |  | sunssf |  |  | 1 |  | R
40086 |  | Hz |  | uint16 | Hz | Hz_SF | supported |  | R | Line Frequency
40087 |  | Hz_SF |  | sunssf |  |  | -2 |  | R
40088 |  | VA |  | int16 | VA | VA_SF | supported |  | R | AC Apparent Power
40089 |  | VA_SF |  | sunssf |  |  | 1 |  | R
40090 |  | Var |  | int16 | var | VAr_SF | supported |  | R | AC Reactive Power
40091 |  | VAr_SF |  | sunssf |  |  | 1 |  | R
40092 |  | PF |  | int16 | Pct | PF_SF | supported |  | R | AC Power Factor | The PF sign ( for RTU/TCP interfaces ) depends from TCP Reactive Sign Convention. Default: EEI
40093 |  | PF_SF |  | sunssf |  |  | -4 |  | R
40094 | WH | WattHours |  | acc32 | Wh | WH_SF | supported |  | R | AC Energy | Total Energy is not provided with model 103 but using model 122 (ActWh)
40096 |  | WH_SF |  | sunssf |  |  | 1 |  | R
40097 | DCA | DC Amps |  | uint16 | A | DCA_SF | supported |  | R | DC Current
40098 |  | DCA_SF |  | sunssf |  |  | -1 |  | R
40099 | DCV | DC Voltage |  | uint16 | V | DCV_SF | unimplemented |  | R | DC Voltage | For this product the DC voltage is not provided with model 103 but using model 160.
40100 |  | DCV_SF |  | sunssf |  |  | unimplemented |  | R
40101 | DCW | DC Watts |  | int16 | W | DCW_SF | supported |  | R | DC Power
40102 |  | DCW_SF |  | sunssf |  |  | 1 |  | R
40103 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | supported |  | R | Cabinet Temperature | This measure is implemented as internal DC wiring-box temperature.
40104 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | supported |  | R | Heat Sink Temperature | This measure is implemented as DC/AC (inverter) stage heatsink temperature.
40105 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | unimplemented |  | R | Transformer Temperature
40106 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | supported |  | R | Other Temperature | This measure is implemented as external ambient temperature.
40107 |  | Tmp_SF |  | sunssf |  |  | -1 |  | R
40108 | St | Operating State |  | enum16 |  |  | supported |  | R | Enumerated value. Operating state
[7 empty] | 1 | Off (OFF) |  |  | This state corresponds to startup phase of inverter controller.
[7 empty] | 2 | Sleeping (SLEEPING) |  |  | This state corresponds to execution of grid interface "auto-test" required by Italian country standard.
[7 empty] | 3 | Starting (STARTING) |  |  | This state corresponds to grid connection phase.
[7 empty] | 4 | MPPT |  |  | This state corresponds to inverter connected to grid and running with MPPT.
[7 empty] | 5 | Throttled (THROTTLED) |  |  | This state corresponds to inverter connected to grid and running with limited active power (derating).
[7 empty] | 6 | Shutting down (SHUTTING_DOWN) |  |  | This state corresponds to forced disconnection from grid (e.g. commanded by user through "remote off" command).
[7 empty] | 7 | Fault (FAULT) |  |  | This state corresponds to fault causing disconnection from grid.
[7 empty] | 8 | Standby (STANDBY) |  |  | This state corresponds to disconnection from grid caused by missing DC source or AC grid.
40109 | StVnd | Vendor Operating State |  | enum16 |  |  | supported |  | R | Vendor specific operating state code
40110 | Evt1 | Event1 |  | bitfield32 |  |  | supported |  | R | Bitmask value. Event fields
[7 empty] | Bit 0 | 1 = Ground fault (GROUND_FAULT) |  |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 = DC over voltage (DC_OVER_VOLT) |  |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | AC disconnect open (AC_DISCONNECT)
[7 empty] | unimplemented | DC disconnect open (DC_DISCONNECT)
[7 empty] | Bit 4 | 1 = Grid shutdown (GRID_DISCONNECT) |  |  | This state corresponds to grid absence.
[7 empty] | unimplemented | Cabinet open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 = Manual shutdown (MANUAL_SHUTDOWN) |  |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 = Over temperature (OVER_TEMP) |  |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | Bit 8 | 1 = Frequency above limit (OVER_FREQUENCY) |  |  | This state corresponds to the following internal alarms: - E006: Grid OF
[7 empty] | Bit 9 | 1 = Frequency under limit (UNDER_FREQUENCY) |  |  | This state corresponds to the following internal alarms: - E007: Grid UF
[7 empty] | Bit 10 | 1 = AC Voltage above limit (AC_OVER_VOLT) |  |  | This state corresponds to the following internal alarms: - E003: Grid OV
[7 empty] | Bit 11 | 1 = AC Voltage under limit (AC_UNDER_VOLT) |  |  | This state corresponds to the following internal alarms: - E004: Grid UV
[7 empty] | unimplemented | Blown String fuse on input (BLOWN_STRING_FUSE)
[7 empty] | Bit 13 | 1 = Under temperature (UNDER_TEMP) |  |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | Bit 14 | 1 = Generic Memory or Communication error (internal) (MEMORY_LOSS) |  |  | This state corresponds to statistics memory fault.
[7 empty] | Bit 15 | 1 = Hardware test failure (HW_TEST_FAILURE) |  |  | This state corresponds to the following internal alarms: - E005: Internal bus fault - E013: Wrong DC input mode - E019: Lekage current self-test fault - E020: Grid interface self-test fault - E021: Grid interface self-test fault - E053: Arc-fault detector self-test fault - E078: R-iso self-test fault
40112 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | supported |  | R | Reserved for future use
40114 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of active power derating: - Bit0: Power curtailment from external command (NOTE: Asserted also for limitation from capability together with bit 12). - Bit1: Power limitation from Frequency-Watt - Bit2: Power limitation from high average grid voltage - Bit3: Power limitation from anti-islanding protection - Bit4: Power limitation from grid current rating limitation - Bit5: Power limitation for high temperature - Bit6: Power limitation for high DC voltage - Bit7: Reserved - Bit8: Power limitation from ramp-rate (connection ramp) - Bit9: Power limitation from momentary cessation - Bit10: Power limitation from ramp-rate (normal ramp-up) - Bit11: Power limitation from Volt-Watt - Bit12: Power limitation from capability (rating) - Bit13-31: Reserved
40116 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of apparent power derating: - Bit0: Power limitation for high temperature - Bit1: Power limitation for high DC voltage - Bit2: Power limitation from capability (rating) - Bit3-31: Reserved
40118 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of auxiliary devices: - Bit0: Fan fault - Bit1: Statistics memory fault - Bit2: RTC clock not set - Bit3: Reserved - Bit4: RTC low battery fault - Bit5: RTC quartz fault - Bit6-31: Reserved
40120 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | Fixed to 0 (reserved for future use)

## 120
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40122 | ID | Nameplate |  | uint16 |  |  | 120 |  |  | Inverter Controls Nameplate Ratings
40123 | L |  |  | uint16 |  |  | 26 |  |  | Model Length
40124 | DERTyp | DERTyp |  | enum16 |  |  | supported |  | R | Type of DER device. Default value is 4 to indicate PV device.
[7 empty] | 4 | PV
[7 empty] | 82 | PV_STOR
40125 | WRtg | WRtg |  | uint16 | W | WRtg_SF | supported |  | R | Continuous power output capability of the inverter. | WRtg represents the max active power capability of the inverter and cannot be modified. Similar considerations apply to all power ratings below.
40126 | WRtg_SF | WRtg_SF |  | sunssf |  |  | 1 |  | R | Scale factor
40127 | VARtg | VARtg |  | uint16 | VA | VARtg_SF | supported |  | R | Continuous Volt-Ampere capability of the inverter.
40128 | VARtg_SF | VARtg_SF |  | sunssf |  |  | 1 |  | R | Scale factor
40129 | VArRtgQ1 | VArRtgQ1 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 1.
40130 | VArRtgQ2 | VArRtgQ2 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 2.
40131 | VArRtgQ3 | VArRtgQ3 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 3.
40132 | VArRtgQ4 | VArRtgQ4 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 4.
40133 | VArRtg_SF | VArRtg_SF |  | sunssf |  |  | 1 |  | R | Scale factor
40134 | ARtg | ARtg |  | uint16 | A | ARtg_SF | supported |  | R | Maximum RMS AC current level capability of the inverter. | Used as reference rating for current ramp-rate on M145.
40135 | ARtg_SF | ARtg_SF |  | sunssf |  |  | 0 |  | R | Scale factor
40136 | PFRtgQ1 | PFRtgQ1 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 1. | The PFRtgQ1 sign ( for RTU/TCP interfaces ) depends from TCP Reactive Sign Convention. Default: EEI
40137 | PFRtgQ2 | PFRtgQ2 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 2.
40138 | PFRtgQ3 | PFRtgQ3 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 3.
40139 | PFRtgQ4 | PFRtgQ4 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 4. | The PFRtgQ4 sign ( for RTU/TCP interfaces ) depends from TCP Reactive Sign Convention. Default: EEI
40140 | PFRtg_SF | PFRtg_SF |  | sunssf |  |  | -3 |  | R | Scale factor
40141 | WHRtg | WHRtg |  | uint16 | Wh | WHRtg_SF | unimplemented |  | R | Nominal energy rating of storage device.
40142 | WHRtg_SF | WHRtg_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor
40143 | AhrRtg | AhrRtg |  | uint16 | AH | AhrRtg_SF | unimplemented |  | R | The useable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating).
40144 | AhrRtg_SF | AhrRtg_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for amp-hour rating.
40145 | MaxChaRte | MaxChaRte |  | uint16 | W | MaxChaRte_SF | unimplemented |  | R | Maximum rate of energy transfer into the storage device.
40146 | MaxChaRte_SF | MaxChaRte_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor
40147 | MaxDisChaRte | MaxDisChaRte |  | uint16 | W | MaxDisChaRte_SF | unimplemented |  | R | Maximum rate of energy transfer out of the storage device.
40148 | MaxDisChaRte_SF | MaxDisChaRte_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor
40149 | Pad | Pad |  | pad |  |  |  |  | R | Pad register.

## 121
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40150 | ID | Basic Settings |  | uint16 |  |  | 121 |  |  | Inverter Controls Basic Settings
40151 | L |  |  | uint16 |  |  | 30 |  |  | Model Length
40152 | WMax | WMax |  | uint16 | W | WMax_SF | supported |  | RW | Setting for maximum power output. Default to WRtg. | WMax represents the max active power capability of the inverter; it can be modified (reduced) respect to WRtg and the modification is intended to be done during fine tuning only. WMax is not intended as register to be written for active power control. Set Point for active power WMaxLimPct [group 123] is expressed as percentage of this register, any change on WMax will influence the behavior of active power set point. The max active power used for power control purposes can be calculated as WMax*10^(WMax_SF). Similar considerations apply to all power ratings below. Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40153 | VRef | VRef |  | uint16 | V | VRef_SF | unimplemented |  | RW | Voltage at the PCC.
40154 | VRefOfs | VRefOfs |  | int16 | V | VRefOfs_SF | unimplemented |  | RW | Offset from PCC to inverter.
40155 | VMax | VMax |  | uint16 | V | VMinMax_SF | unimplemented |  | RW | Setpoint for maximum voltage.
40156 | VMin | VMin |  | uint16 | V | VMinMax_SF | unimplemented |  | RW | Setpoint for minimum voltage.
40157 | VAMax | VAMax |  | uint16 | VA | VAMax_SF | supported |  | RW | Setpoint for maximum apparent power. Default to VARtg. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40158 | VArMaxQ1 | VArMaxQ1 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | Since reactive power limit is equally applied on all quadrants, the same parameter value is actually exposed on VArMaxQ1, VArMaxQ2, VArMaxQ3 and VArMaxQ4. This produces the following consequences: - When one of these registers is written, the same value (if accepted) will be read on the others; - When multiple registers are written, only the last change is applied; In addition, if VArMax is changed when VArPct control (M123) is enabled in VArMax mode, it is necessary to disable and enable again the VArPct control or restart the logical controller (e.g. cycling power feed) in order to use the new VArMax limit. Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40159 | VArMaxQ2 | VArMaxQ2 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2.
40160 | VArMaxQ3 | VArMaxQ3 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3.
40161 | VArMaxQ4 | VArMaxQ4 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4.
40162 | WGra | WGra |  | uint16 | % WMax/sec | WGra_SF | supported |  | RW | Default ramp rate of change of active power due to command or internal action. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40163 | PFMinQ1 | PFMinQ1 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1.
40164 | PFMinQ2 | PFMinQ2 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2.
40165 | PFMinQ3 | PFMinQ3 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3.
40166 | PFMinQ4 | PFMinQ4 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4.
40167 | VArAct | VArAct |  | enum16 |  |  | unimplemented |  | RW | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization.
40168 | ClcTotVA | ClcTotVA |  | enum16 |  |  | unimplemented |  | RW | Calculation method for total apparent power. 1=vector 2=arithmetic.
40169 | MaxRmpRte | MaxRmpRte |  | uint16 | % WGra | MaxRmpRte_SF | unimplemented |  | RW | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.
40170 | ECPNomHz | ECPNomHz |  | uint16 | Hz | ECPNomHz_SF | unimplemented |  | RW | Setpoint for nominal frequency at the ECP.
40171 | ConnPh | ConnPh |  | enum16 |  |  | unimplemented |  | RW | Identity of connected phase for single phase inverters. A=1 B=2 C=3.
40172 | WMax_SF | WMax_SF |  | sunssf |  |  | 1 |  | R | Scale factor for real power.
40173 | VRef_SF | VRef_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for voltage at the PCC.
40174 | VRefOfs_SF | VRefOfs_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for offset voltage.
40175 | VMinMax_SF | VMinMax_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for min/max voltages.
40176 | VAMax_SF | VAMax_SF |  | sunssf |  |  | 1 |  | R | Scale factor for apparent power.
40177 | VArMax_SF | VArMax_SF |  | sunssf |  |  | 1 |  | R | Scale factor for reactive power.
40178 | WGra_SF | WGra_SF |  | sunssf |  |  | -1 |  | R | Scale factor for default ramp rate.
40179 | PFMin_SF | PFMin_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for minimum power factor.
40180 | MaxRmpRte_SF | MaxRmpRte_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for maximum ramp percentage.
40181 | ECPNomHz_SF | ECPNomHz_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for nominal frequency.

## 122
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40182 | ID | Measurements_Status |  | uint16 |  |  | 122 |  |  | Inverter Controls Extended Measurements and Status
40183 | L |  |  | uint16 |  |  | 44 |  |  | Model Length
40184 | PVConn | PVConn |  | bitfield16 |  |  | supported |  | R | PV inverter present/available status. Enumerated value.
[7 empty] | Bit 0 | 1 = CONNECTED
[7 empty] | unimplemented | AVAILABLE
[7 empty] | unimplemented | OPERATING
[7 empty] | unimplemented | TEST
40185 | StorConn | StorConn |  | bitfield16 |  |  | supported |  | R | Storage inverter present/available status. Enumerated value.
[7 empty] | unimplemented | CONNECTED
[7 empty] | unimplemented | AVAILABLE
[7 empty] | unimplemented | OPERATING
[7 empty] | unimplemented | TEST
40186 | ECPConn | ECPConn |  | bitfield16 |  |  | supported |  | R | ECP connection status: disconnected=0 connected=1.
[7 empty] | Bit 0 | 1 = CONNECTED
40187 | ActWh | ActWh |  | acc64 | Wh |  | supported |  | R | AC lifetime active (real) energy output. | Total exported active energy
40191 | ActVAh | ActVAh |  | acc64 | VAh |  | supported |  | R | AC lifetime apparent energy output. | Total exported apparent energy
40195 | ActVArhQ1 | ActVArhQ1 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime reactive energy output in quadrant 1.
40199 | ActVArhQ2 | ActVArhQ2 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime reactive energy output in quadrant 2.
40203 | ActVArhQ3 | ActVArhQ3 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime negative energy output in quadrant 3.
40207 | ActVArhQ4 | ActVArhQ4 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime reactive energy output in quadrant 4.
40211 | VArAval | VArAval |  | int16 | var | VArAval_SF | unimplemented |  | R | Amount of VARs available without impacting watts output.
40212 | VArAval_SF | VArAval_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for available VARs.
40213 | WAval | WAval |  | uint16 | var | WAval_SF | unimplemented |  | R | Amount of Watts available.
40214 | WAval_SF | WAval_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for available Watts.
40215 | StSetLimMsk | StSetLimMsk |  | bitfield32 |  |  | supported |  | R | Bit Mask indicating setpoint limit(s) reached.
[7 empty] | Bit 0 | 1 = WMax
[7 empty] | Bit 1 | 1 = VAMax
[7 empty] | unimplemented | VArAval
[7 empty] | Bit 3 | 1 = VArMaxQ1 |  |  | Since reactive power operates with the same limit on all quadrants, bits VArMaxQ1, VArMaxQ2, VArMaxQ3, VArMaxQ4 are set together.
[7 empty] | Bit 4 | 1 = VArMaxQ2
[7 empty] | Bit 5 | 1 = VArMaxQ3
[7 empty] | Bit 6 | 1 = VArMaxQ4
[7 empty] | unimplemented | PFMinQ1
[7 empty] | unimplemented | PFMinQ2
[7 empty] | unimplemented | PFMinQ3
[7 empty] | unimplemented | PFMinQ4
40217 | StActCtl | StActCtl |  | bitfield32 | 0 | 0 | supported |  | R | Bit Mask indicating which inverter controls are currently active.
[7 empty] | Bit 0 | 1 = FixedW
[7 empty] | Bit 1 | 1 = FixedVAR
[7 empty] | Bit 2 | 1 = FixedPF
[7 empty] | unimplemented | Volt-VAr
[7 empty] | unimplemented | Freq-Watt-Param
[7 empty] | unimplemented | Freq-Watt-Curve
[7 empty] | unimplemented | Dyn-Reactive-Current
[7 empty] | unimplemented | LVRT
[7 empty] | unimplemented | HVRT
[7 empty] | unimplemented | Watt-PF
[7 empty] | unimplemented | Volt-Watt
[7 empty] | unimplemented | Scheduled
[7 empty] | unimplemented | LFRT
[7 empty] | unimplemented | HFRT
40219 | TmSrc | TmSrc |  | string |  |  | unimplemented |  | R | Source of time synchronization.
40223 | Tms | Tms |  | uint32 | Secs |  | supported |  | R | Seconds since 01-01-2000 00:00 UTC
40225 | RtSt | RtSt |  | bitfield16 |  |  | supported |  | R | Bit Mask indicating active ride-through status.
[7 empty] | Bit 0 | 1 = LVRT_ACTIVE |  |  | This state is referred to activation of "momentary cessation" ride-through protection.
[7 empty] | Bit 1 | 1 = HVRT_ACTIVE |  |  | This state is referred to activation of "momentary cessation" ride-through protection.
[7 empty] | Bit 2 | 1 = LFRT_ACTIVE |  |  | This state is referred to activation of "momentary cessation" ride-through protection.
[7 empty] | Bit 3 | 1 = HFRT_ACTIVE |  |  | This state is referred to activation of "momentary cessation" ride-through protection.
40226 | Ris | Ris |  | uint16 | ohms | Ris_SF | supported |  | R | Isolation resistance.
40227 | Ris_SF | Ris_SF |  | sunssf |  |  | 3 |  | R | Scale factor for isolation resistance.

## 123
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40228 | ID | Immediate Controls |  | uint16 |  |  | 123 |  |  | Immediate Inverter Controls | i. MaxLimPct: represents the target set-point of the active power control. - The set-point is expressed as % of WMax [group 121]; - The set point is calculated as WMaxLimPct *10^( WMaxLimPct_SF); - The target ouput power of the inverter is then calculated as WMax*10^(WMax_SF)*[WMaxLimPct *10^( WMaxLimPct_SF)]/100. ii. WMaxLimPct_WinTms: the time window is a period of time within which the inverter randomly delays before beginning execution of the command. iii. WMaxLimPct_RvrtTms: the reversion timeout value (if not zero) specifies a time for the requested change to revert to its default state. A timeout value of zero means the change persists until another change is made. If a reversion timer expires the control reverts to its default state. A timeout value of zero shall be avoided for closed loop control purpose. iv. WMaxLimPct_RmpTms: the ramp time is a fixed time in seconds, over which the inverter settings are to transition from their pre—setting level to their post—settings level v. WMaxLim_Ena represents the enable for the active power management according to the previously described 4 registers. WMaxLim_Ena is set at 0 by default and must be written to 1 to enable the active power reduction according to previous registers; In dynamic control funcitioning, the set-point is expected to be updated before the revision time WMaxLimPct_RvrtTms expires. To make effective the new active power settings it is needed to overwrite 1 to the enable WMaxLim_Ena register. Similar considerations apply to reactive power and power factor controls.
40229 | L |  |  | uint16 |  |  | 24 |  |  | Model Length
40230 | Conn_WinTms | Conn_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for connect/disconnect.
40231 | Conn_RvrtTms | Conn_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for connect/disconnect.
40232 | Conn | Conn |  | enum16 |  |  | supported |  | RW | Enumerated valued. Connection control.
[7 empty] | 0 | DISCONNECT
[7 empty] | 1 | CONNECT
40233 | WMaxLimPct | WMaxLimPct |  | uint16 | % WMax | WMaxLimPct_SF | supported |  | RW | Set power output to specified level.
40234 | WMaxLimPct_WinTms | WMaxLimPct_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for power limit change.
40235 | WMaxLimPct_RvrtTms | WMaxLimPct_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for power limit. | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the control settings will be saved on non-volatile storage and so the user application shall not send frequent commands using RvrtTms = 0 because this can damage the memory support.
40236 | WMaxLimPct_RmpTms | WMaxLimPct_RmpTms |  | uint16 | Secs |  | supported |  | RW | Ramp time for moving from current setpoint to new setpoint.
40237 | WMaxLim_Ena | WMaxLim_Ena |  | enum16 |  |  | supported |  | RW | Enumerated valued. Throttle enable/disable control.
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
40238 | OutPFSet | OutPFSet |  | int16 | cos() | OutPFSet_SF | supported |  | RW | Set power factor to specific value - cosine of angle.
40239 | OutPFSet_WinTms | OutPFSet_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for power factor change.
40240 | OutPFSet_RvrtTms | OutPFSet_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for power factor. | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not send frequent commands using RvrtTms = 0 because this can damage the memory support. In case RvtTms > 0 is sent, "default" settings will be restored when reversion time is expired.
40241 | OutPFSet_RmpTms | OutPFSet_RmpTms |  | uint16 | Secs |  | supported |  | RW | Ramp time for moving from current setpoint to new setpoint.
40242 | OutPFSet_Ena | OutPFSet_Ena |  | enum16 |  |  | supported |  | RW | Enumerated valued. Fixed power factor enable/disable control.
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
40243 | VArWMaxPct | VArWMaxPct |  | int16 | % WMax | VArPct_SF | supported |  | RW | Reactive power in percent of WMax. | Before to write and enable this set point, register VArPct_Mod shall be properly configured
40244 | VArMaxPct | VArMaxPct |  | int16 | % VArMax | VArPct_SF | supported |  | RW | Reactive power in percent of VArMax. | Before to write and enable this set point, register VArPct_Mod shall be properly configured
40245 | VArAvalPct | VArAvalPct |  | int16 | % VArAval | VArPct_SF | unimplemented |  | RW | Reactive power in percent of VArAval.
40246 | VArPct_WinTms | VArPct_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for VAR limit change.
40247 | VArPct_RvrtTms | VArPct_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for VAR limit. | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not send frequent commands using RvrtTms = 0 because this can damage the memory support. In case RvtTms > 0 is sent, "default" settings will be restored when reversion time is expired.
40248 | VArPct_RmpTms | VArPct_RmpTms |  | uint16 | Secs |  | supported |  | RW | Ramp time for moving from current setpoint to new setpoint.
40249 | VArPct_Mod | VArPct_Mod |  | enum16 |  |  | supported |  | RW | Enumerated value. VAR percent limit mode. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | unimplemented | NONE |  |  | Default value to NONE
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40250 | VArPct_Ena | VArPct_Ena |  | enum16 |  |  | supported |  | RW | Enumerated valued. Percent limit VAr enable/disable control.
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
40251 | WMaxLimPct_SF | WMaxLimPct_SF |  | sunssf |  |  | -1 |  | R | Scale factor for power output percent.
40252 | OutPFSet_SF | OutPFSet_SF |  | sunssf |  |  | -4 |  | R | Scale factor for power factor.
40253 | VArPct_SF | VArPct_SF |  | sunssf |  |  | -1 |  | R | Scale factor for reactive power percent.

## 126
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40254 | ID | Static Volt-VAR |  | uint16 |  |  | 126 |  |  | Static Volt-VAR Arrays | Monotony of curve: X values (Vn) for Volt-VAR curve must be arranged in a monotonic increasing sequence. Limitation: We can write MAX 2 couple of values (Vx-VArx) at once
40255 | L |  |  | uint16 |  |  | 226 |  |  | Model Length
40256 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40257 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | Is Volt-VAR control active.
[7 empty] | Bit 0 | 1 = ENABLED
40258 | WinTms | WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for volt-VAR change. | WinTms is placed in subsequent address respect to ModEna register. If WinTms is written after having written 1 on ModEna for enabling the control, the new WinTms value is not applied (because the WinTms setting is acquired immediately when control is enabled). This means that the client application must write the desired time on WinTms register before writing 1 on ModEna for enabling the control.
40259 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for volt-VAR curve selection.
40260 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40261 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40262 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximum of 20).
40263 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40264 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | -1 |  | R | scale factor for dependent variable.
40265 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | 0 |  | R | Scale factor for increment and decrement ramps.
40266 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40267 | DeptRef | DeptRef | 1 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40268 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40269 | VAr1 | VAr1 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40270 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40271 | VAr2 | VAr2 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40272 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40273 | VAr3 | VAr3 | 1 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40274 | V4 | V4 | 1 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40275 | VAr4 | VAr4 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40276 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40277 | VAr5 | VAr5 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40278 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40279 | VAr6 | VAr6 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40280 | V7 | V7 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40281 | VAr7 | VAr7 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40282 | V8 | V8 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40283 | VAr8 | VAr8 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40284 | V9 | V9 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40285 | VAr9 | VAr9 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40286 | V10 | V10 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40287 | VAr10 | VAr10 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40288 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40289 | VAr11 | VAr11 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40290 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40291 | VAr12 | VAr12 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40292 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40293 | VAr13 | VAr13 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40294 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40295 | VAr14 | VAr14 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40296 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40297 | VAr15 | VAr15 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40298 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40299 | VAr16 | VAr16 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40300 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40301 | VAr17 | VAr17 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40302 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40303 | VAr18 | VAr18 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40304 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40305 | VAr19 | VAr19 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40306 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40307 | VAr20 | VAr20 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40308 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve. (Max 16 chars)
40316 | RmpTms |  | 1 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40317 | RmpDecTmm | RmpDecTmm | 1 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40318 | RmpIncTmm | RmpIncTmm | 1 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40319 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
40320 | ActPt | ActPt | 2 | uint16 |  |  | supported |  | RW | Number of active points in array.
40321 | DeptRef | DeptRef | 2 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40322 | V1 | V1 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40323 | VAr1 | VAr1 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40324 | V2 | V2 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40325 | VAr2 | VAr2 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40326 | V3 | V3 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40327 | VAr3 | VAr3 | 2 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40328 | V4 | V4 | 2 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40329 | VAr4 | VAr4 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40330 | V5 | V5 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40331 | VAr5 | VAr5 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40332 | V6 | V6 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40333 | VAr6 | VAr6 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40334 | V7 | V7 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40335 | VAr7 | VAr7 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40336 | V8 | V8 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40337 | VAr8 | VAr8 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40338 | V9 | V9 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40339 | VAr9 | VAr9 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40340 | V10 | V10 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40341 | VAr10 | VAr10 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40342 | V11 | V11 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40343 | VAr11 | VAr11 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40344 | V12 | V12 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40345 | VAr12 | VAr12 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40346 | V13 | V13 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40347 | VAr13 | VAr13 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40348 | V14 | V14 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40349 | VAr14 | VAr14 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40350 | V15 | V15 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40351 | VAr15 | VAr15 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40352 | V16 | V16 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40353 | VAr16 | VAr16 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40354 | V17 | V17 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40355 | VAr17 | VAr17 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40356 | V18 | V18 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40357 | VAr18 | VAr18 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40358 | V19 | V19 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40359 | VAr19 | VAr19 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40360 | V20 | V20 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40361 | VAr20 | VAr20 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40362 | CrvNam | CrvNam | 2 | string |  |  | supported |  | RW | Optional description for curve. (Max 16 chars)
40370 | RmpTms |  | 2 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40371 | RmpDecTmm | RmpDecTmm | 2 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40372 | RmpIncTmm | RmpIncTmm | 2 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40373 | ReadOnly | ReadOnly | 2 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
40374 | ActPt | ActPt | 3 | uint16 |  |  | supported |  | RW | Number of active points in array.
40375 | DeptRef | DeptRef | 3 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40376 | V1 | V1 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40377 | VAr1 | VAr1 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40378 | V2 | V2 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40379 | VAr2 | VAr2 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40380 | V3 | V3 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40381 | VAr3 | VAr3 | 3 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40382 | V4 | V4 | 3 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40383 | VAr4 | VAr4 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40384 | V5 | V5 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40385 | VAr5 | VAr5 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40386 | V6 | V6 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40387 | VAr6 | VAr6 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40388 | V7 | V7 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40389 | VAr7 | VAr7 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40390 | V8 | V8 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40391 | VAr8 | VAr8 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40392 | V9 | V9 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40393 | VAr9 | VAr9 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40394 | V10 | V10 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40395 | VAr10 | VAr10 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40396 | V11 | V11 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40397 | VAr11 | VAr11 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40398 | V12 | V12 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40399 | VAr12 | VAr12 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40400 | V13 | V13 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40401 | VAr13 | VAr13 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40402 | V14 | V14 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40403 | VAr14 | VAr14 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40404 | V15 | V15 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40405 | VAr15 | VAr15 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40406 | V16 | V16 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40407 | VAr16 | VAr16 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40408 | V17 | V17 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40409 | VAr17 | VAr17 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40410 | V18 | V18 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40411 | VAr18 | VAr18 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40412 | V19 | V19 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40413 | VAr19 | VAr19 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40414 | V20 | V20 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40415 | VAr20 | VAr20 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40416 | CrvNam | CrvNam | 3 | string |  |  | supported |  | RW | Optional description for curve. (Max 16 chars)
40424 | RmpTms |  | 3 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40425 | RmpDecTmm | RmpDecTmm | 3 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40426 | RmpIncTmm | RmpIncTmm | 3 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40427 | ReadOnly | ReadOnly | 3 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
40428 | ActPt | ActPt | 4 | uint16 |  |  | supported |  | RW | Number of active points in array.
40429 | DeptRef | DeptRef | 4 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40430 | V1 | V1 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40431 | VAr1 | VAr1 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40432 | V2 | V2 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40433 | VAr2 | VAr2 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40434 | V3 | V3 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40435 | VAr3 | VAr3 | 4 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40436 | V4 | V4 | 4 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40437 | VAr4 | VAr4 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40438 | V5 | V5 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40439 | VAr5 | VAr5 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40440 | V6 | V6 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40441 | VAr6 | VAr6 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40442 | V7 | V7 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40443 | VAr7 | VAr7 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40444 | V8 | V8 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40445 | VAr8 | VAr8 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40446 | V9 | V9 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40447 | VAr9 | VAr9 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40448 | V10 | V10 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40449 | VAr10 | VAr10 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40450 | V11 | V11 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40451 | VAr11 | VAr11 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40452 | V12 | V12 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40453 | VAr12 | VAr12 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40454 | V13 | V13 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40455 | VAr13 | VAr13 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40456 | V14 | V14 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40457 | VAr14 | VAr14 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40458 | V15 | V15 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40459 | VAr15 | VAr15 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40460 | V16 | V16 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40461 | VAr16 | VAr16 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40462 | V17 | V17 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40463 | VAr17 | VAr17 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40464 | V18 | V18 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40465 | VAr18 | VAr18 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40466 | V19 | V19 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40467 | VAr19 | VAr19 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40468 | V20 | V20 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40469 | VAr20 | VAr20 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40470 | CrvNam | CrvNam | 4 | string |  |  | supported |  | RW | Optional description for curve. (Max 16 chars)
40478 | RmpTms |  | 4 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40479 | RmpDecTmm | RmpDecTmm | 4 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40480 | RmpIncTmm | RmpIncTmm | 4 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40481 | ReadOnly | ReadOnly | 4 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 127
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40482 | ID | Freq-Watt Param |  | uint16 |  |  | 127 |  |  | Parameterized Frequency-Watt
40483 | L |  |  | uint16 |  |  | 10 |  |  | Model Length
40484 | WGra | WGra |  | uint16 | % PM/Hz | WGra_SF | supported |  | RW | The slope of the reduction in the maximum allowed watts output as a function of frequency. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40485 | HzStr | HzStr |  | int16 | Hz | HzStrStop_SF | supported |  | RW | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs.
40486 | HzStop | HzStop |  | int16 | Hz | HzStrStop_SF | supported |  | RW | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed.
40487 | HysEna | HysEna |  | bitfield16 |  |  | supported |  | RW | Enable hysterisis
[7 empty] | Bit 0 | 1 = ENABLED
40488 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | Is Parameterized Frequency-Watt control active.
[7 empty] | Bit 0 | 1 = ENABLED
40489 | HzStopWGra | HzStopWGra |  | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event.
40490 | WGra_SF | WGra_SF |  | sunssf |  |  | 0 |  | R | Scale factor for output gradient.
40491 | HzStrStop_SF | HzStrStop_SF |  | sunssf |  |  | -2 |  | R | Scale factor for frequency deviations.
40492 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | 0 |  | R | Scale factor for increment and decrement ramps.
40493 | Pad |  |  | pad |  |  |  |  | R

## 129
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40494 | ID | LVRTD |  | uint16 |  |  | 129 |  |  | LVRT Must Disconnect
40495 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40496 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve.
40497 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED
40498 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for LVRT change.
40499 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for LVRT curve selection.
40500 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40501 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40502 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
40503 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40504 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40505 | Pad |  |  | pad |  |  |  |  | R
40506 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40507 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40508 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 must disconnect voltage.
40509 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40510 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 must disconnect voltage.
40511 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40512 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 must disconnect voltage.
40513 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40514 | V4 | V4 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 must disconnect voltage.
40515 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40516 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 must disconnect voltage.
40517 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40518 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 must disconnect voltage.
40519 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40520 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 must disconnect voltage.
40521 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40522 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 must disconnect voltage.
40523 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40524 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 must disconnect voltage.
40525 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40526 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 must disconnect voltage.
40527 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40528 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 must disconnect voltage.
40529 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40530 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 must disconnect voltage.
40531 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40532 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 must disconnect voltage.
40533 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40534 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 must disconnect voltage.
40535 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40536 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 must disconnect voltage.
40537 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40538 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 must disconnect voltage.
40539 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40540 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 must disconnect voltage.
40541 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40542 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 must disconnect voltage.
40543 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40544 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 must disconnect voltage.
40545 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40546 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 must disconnect voltage.
40547 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
40555 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 130
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40556 | ID | HVRTD |  | uint16 |  |  | 130 |  |  | HVRT Must Disconnect
40557 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40558 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve.
40559 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | HVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED
40560 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for HVRT change.
40561 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for HVRT curve selection.
40562 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40563 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40564 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
40565 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40566 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40567 | Pad |  |  | pad |  |  |  |  | R
40568 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40569 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40570 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 must disconnect voltage.
40571 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40572 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 must disconnect voltage.
40573 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40574 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 must disconnect voltage.
40575 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40576 | V4 | V4 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 must disconnect voltage.
40577 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40578 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 must disconnect voltage.
40579 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40580 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 must disconnect voltage.
40581 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40582 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 must disconnect voltage.
40583 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40584 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 must disconnect voltage.
40585 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40586 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 must disconnect voltage.
40587 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40588 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 must disconnect voltage.
40589 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40590 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 must disconnect voltage.
40591 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40592 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 must disconnect voltage.
40593 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40594 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 must disconnect voltage.
40595 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40596 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 must disconnect voltage.
40597 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40598 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 must disconnect voltage.
40599 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40600 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 must disconnect voltage.
40601 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40602 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 must disconnect voltage.
40603 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40604 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 must disconnect voltage.
40605 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40606 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 must disconnect voltage.
40607 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40608 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 must disconnect voltage.
40609 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
40617 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 132
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40618 | ID | Volt-Watt |  | uint16 |  |  | 132 |  |  | Volt-Watt | Monotony of curve: X values (Vn) for Volt-Watt curve must be arranged in a monotonic increasing sequence. Limitation: We can write MAX 2 couple of values (Vx-Wx) at once
40619 | L |  |  | uint16 |  |  | 226 |  |  | Model Length
40620 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40621 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | Is Volt-Watt control active.
[7 empty] | Bit 0 | 1 = ENABLED
40622 | WinTms | WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for volt-watt change. | WinTms is placed in subsequent address respect to ModEna register. If WinTms is written after having written 1 on ModEna for enabling the control, the new WinTms value is not applied (because the WinTms setting is acquired immediately when control is enabled). This means that the client application must write the desired time on WinTms register before writing 1 on ModEna for enabling the control.
40623 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for volt-watt curve selection.
40624 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40625 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend min. 4).
40626 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of points in array (maximum 20).
40627 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40628 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | -1 |  | R | Scale Factor for % DeptRef
40629 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | 0 |  | R | Scale factor for increment and decrement ramps.
40630 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40631 | DeptRef | DeptRef | 1 | enum16 |  |  | supported |  | RW | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | 1 | %WMax
[7 empty] | unimplemented | %WAval
40632 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40633 | W1 | W1 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40634 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40635 | W2 | W2 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40636 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40637 | W3 | W3 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40638 | V4 | V4 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40639 | W4 | W4 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40640 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40641 | W5 | W5 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40642 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40643 | W6 | W6 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40644 | V7 | V7 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40645 | W7 | W7 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40646 | V8 | V8 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40647 | W8 | W8 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40648 | V9 | V9 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40649 | W9 | W9 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40650 | V10 | V10 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40651 | W10 | W10 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40652 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40653 | W11 | W11 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40654 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40655 | W12 | W12 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40656 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40657 | W13 | W13 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40658 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40659 | W14 | W14 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40660 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40661 | W15 | W15 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40662 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40663 | W16 | W16 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40664 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40665 | W17 | W17 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40666 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40667 | W18 | W18 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40668 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40669 | W19 | W19 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40670 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40671 | W20 | W20 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40672 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
40680 | RmpPt1Tms | RmpPt1Tms | 1 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40681 | RmpDecTmm | RmpDecTmm | 1 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40682 | RmpIncTmm | RmpIncTmm | 1 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40683 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
40684 | ActPt | ActPt | 2 | uint16 |  |  | supported |  | RW | Number of active points in array.
40685 | DeptRef | DeptRef | 2 | enum16 |  |  | supported |  | RW | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40686 | V1 | V1 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40687 | W1 | W1 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40688 | V2 | V2 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40689 | W2 | W2 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40690 | V3 | V3 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40691 | W3 | W3 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40692 | V4 | V4 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40693 | W4 | W4 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40694 | V5 | V5 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40695 | W5 | W5 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40696 | V6 | V6 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40697 | W6 | W6 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40698 | V7 | V7 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40699 | W7 | W7 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40700 | V8 | V8 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40701 | W8 | W8 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40702 | V9 | V9 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40703 | W9 | W9 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40704 | V10 | V10 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40705 | W10 | W10 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40706 | V11 | V11 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40707 | W11 | W11 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40708 | V12 | V12 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40709 | W12 | W12 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40710 | V13 | V13 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40711 | W13 | W13 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40712 | V14 | V14 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40713 | W14 | W14 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40714 | V15 | V15 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40715 | W15 | W15 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40716 | V16 | V16 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40717 | W16 | W16 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40718 | V17 | V17 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40719 | W17 | W17 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40720 | V18 | V18 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40721 | W18 | W18 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40722 | V19 | V19 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40723 | W19 | W19 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40724 | V20 | V20 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40725 | W20 | W20 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40726 | CrvNam | CrvNam | 2 | string |  |  | supported |  | RW | Optional description for curve.
40734 | RmpPt1Tms | RmpPt1Tms | 2 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40735 | RmpDecTmm | RmpDecTmm | 2 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40736 | RmpIncTmm | RmpIncTmm | 2 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40737 | ReadOnly | ReadOnly | 2 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
40738 | ActPt | ActPt | 3 | uint16 |  |  | supported |  | RW | Number of active points in array.
40739 | DeptRef | DeptRef | 3 | enum16 |  |  | supported |  | RW | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40740 | V1 | V1 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40741 | W1 | W1 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40742 | V2 | V2 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40743 | W2 | W2 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40744 | V3 | V3 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40745 | W3 | W3 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40746 | V4 | V4 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40747 | W4 | W4 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40748 | V5 | V5 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40749 | W5 | W5 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40750 | V6 | V6 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40751 | W6 | W6 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40752 | V7 | V7 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40753 | W7 | W7 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40754 | V8 | V8 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40755 | W8 | W8 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40756 | V9 | V9 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40757 | W9 | W9 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40758 | V10 | V10 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40759 | W10 | W10 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40760 | V11 | V11 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40761 | W11 | W11 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40762 | V12 | V12 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40763 | W12 | W12 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40764 | V13 | V13 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40765 | W13 | W13 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40766 | V14 | V14 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40767 | W14 | W14 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40768 | V15 | V15 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40769 | W15 | W15 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40770 | V16 | V16 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40771 | W16 | W16 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40772 | V17 | V17 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40773 | W17 | W17 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40774 | V18 | V18 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40775 | W18 | W18 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40776 | V19 | V19 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40777 | W19 | W19 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40778 | V20 | V20 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40779 | W20 | W20 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40780 | CrvNam | CrvNam | 3 | string |  |  | supported |  | RW | Optional description for curve.
40788 | RmpPt1Tms | RmpPt1Tms | 3 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40789 | RmpDecTmm | RmpDecTmm | 3 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40790 | RmpIncTmm | RmpIncTmm | 3 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40791 | ReadOnly | ReadOnly | 3 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
40792 | ActPt | ActPt | 4 | uint16 |  |  | supported |  | RW | Number of active points in array.
40793 | DeptRef | DeptRef | 4 | enum16 |  |  | supported |  | RW | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40794 | V1 | V1 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts.
40795 | W1 | W1 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40796 | V2 | V2 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40797 | W2 | W2 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40798 | V3 | V3 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40799 | W3 | W3 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40800 | V4 | V4 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40801 | W4 | W4 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40802 | V5 | V5 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40803 | W5 | W5 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40804 | V6 | V6 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40805 | W6 | W6 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40806 | V7 | V7 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40807 | W7 | W7 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40808 | V8 | V8 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40809 | W8 | W8 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40810 | V9 | V9 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40811 | W9 | W9 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40812 | V10 | V10 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40813 | W10 | W10 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40814 | V11 | V11 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40815 | W11 | W11 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40816 | V12 | V12 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40817 | W12 | W12 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40818 | V13 | V13 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40819 | W13 | W13 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40820 | V14 | V14 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40821 | W14 | W14 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40822 | V15 | V15 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40823 | W15 | W15 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40824 | V16 | V16 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40825 | W16 | W16 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40826 | V17 | V17 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40827 | W17 | W17 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40828 | V18 | V18 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40829 | W18 | W18 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40830 | V19 | V19 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40831 | W19 | W19 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40832 | V20 | V20 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40833 | W20 | W20 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40834 | CrvNam | CrvNam | 4 | string |  |  | supported |  | RW | Optional description for curve.
40842 | RmpPt1Tms | RmpPt1Tms | 4 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40843 | RmpDecTmm | RmpDecTmm | 4 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40844 | RmpIncTmm | RmpIncTmm | 4 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40845 | ReadOnly | ReadOnly | 4 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.

## 135
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40846 | ID | LFRT |  | uint16 |  |  | 135 |  |  | Low Frequency Ride-through
40847 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40848 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve.
40849 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LHzRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED
40850 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for LFRT change.
40851 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for LFRT curve selection.
40852 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40853 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40854 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
40855 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40856 | Hz_SF | Hz_SF |  | sunssf |  |  | -2 |  | R | Scale factor for frequency.
40857 | Pad |  |  | pad |  |  |  |  | R
40858 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40859 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40860 | Hz1 | Hz1 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 1 must disconnect frequency.
40861 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40862 | Hz2 | Hz2 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 2 must disconnect frequency.
40863 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40864 | Hz3 | Hz3 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 3 must disconnect frequency.
40865 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40866 | Hz4 | Hz4 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 4 must disconnect frequency.
40867 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40868 | Hz5 | Hz5 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 5 must disconnect frequency.
40869 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40870 | Hz6 | Hz6 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 6 must disconnect frequency.
40871 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40872 | Hz7 | Hz7 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 7 must disconnect frequency.
40873 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40874 | Hz8 | Hz8 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 8 must disconnect frequency.
40875 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40876 | Hz9 | Hz9 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 9 must disconnect frequency.
40877 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40878 | Hz10 | Hz10 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 10 must disconnect frequency.
40879 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40880 | Hz11 | Hz11 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 11 must disconnect frequency.
40881 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40882 | Hz12 | Hz12 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 12 must disconnect frequency.
40883 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40884 | Hz13 | Hz13 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 13 must disconnect frequency.
40885 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40886 | Hz14 | Hz14 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 14 must disconnect frequency.
40887 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40888 | Hz15 | Hz15 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 15 must disconnect frequency.
40889 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40890 | Hz16 | Hz16 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 16 must disconnect frequency.
40891 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40892 | Hz17 | Hz17 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 17 must disconnect frequency.
40893 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40894 | Hz18 | Hz18 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 18 must disconnect frequency.
40895 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40896 | Hz19 | Hz19 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 19 must disconnect frequency.
40897 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40898 | Hz20 | Hz20 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 20 must disconnect frequency.
40899 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
40907 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 136
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40908 | ID | HFRT |  | uint16 |  |  | 136 |  |  | High Frequency Ride-through
40909 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40910 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve.
40911 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | HFRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED
40912 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for HFRT change.
40913 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for HFRT curve selection.
40914 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40915 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40916 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
40917 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40918 | Hz_SF | Hz_SF |  | sunssf |  |  | -2 |  | R | Scale factor for frequency.
40919 | Pad |  |  | pad |  |  |  |  | R
40920 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40921 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40922 | Hz1 | Hz1 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 1 must disconnect frequency.
40923 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40924 | Hz2 | Hz2 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 2 must disconnect frequency.
40925 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40926 | Hz3 | Hz3 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 3 must disconnect frequency.
40927 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40928 | Hz4 | Hz4 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 4 must disconnect frequency.
40929 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40930 | Hz5 | Hz5 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 5 must disconnect frequency.
40931 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40932 | Hz6 | Hz6 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 6 must disconnect frequency.
40933 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40934 | Hz7 | Hz7 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 7 must disconnect frequency.
40935 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40936 | Hz8 | Hz8 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 8 must disconnect frequency.
40937 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40938 | Hz9 | Hz9 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 9 must disconnect frequency.
40939 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40940 | Hz10 | Hz10 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 10 must disconnect frequency.
40941 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40942 | Hz11 | Hz11 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 11 must disconnect frequency.
40943 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40944 | Hz12 | Hz12 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 12 must disconnect frequency.
40945 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40946 | Hz13 | Hz13 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 13 must disconnect frequency.
40947 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40948 | Hz14 | Hz14 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 14 must disconnect frequency.
40949 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40950 | Hz15 | Hz15 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 15 must disconnect frequency.
40951 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40952 | Hz16 | Hz16 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 16 must disconnect frequency.
40953 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40954 | Hz17 | Hz17 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 17 must disconnect frequency.
40955 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40956 | Hz18 | Hz18 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 18 must disconnect frequency.
40957 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40958 | Hz19 | Hz19 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 19 must disconnect frequency.
40959 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40960 | Hz20 | Hz20 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 20 must disconnect frequency.
40961 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
40969 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 139
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40970 | ID | LVRTX |  | uint16 |  |  | 139 |  |  | LVRT extended curve
40971 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40972 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve.
40973 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED |  |  | The enable of LVRT is shared with HVRT so setting this bit has the same effect on "ModEna" register of M140.
40974 | WinTms | WinTms |  | uint16 | Secs |  | unimplemented |  | RW | Time window for LVRT change.
40975 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for LVRT curve selection.
40976 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40977 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40978 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
40979 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40980 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40981 | CrvType |  |  | enum16 |  |  | supported |  | R
[7 empty] | 1 | CEASE_TO_ENERGIZE
40982 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40983 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 1 duration.
40984 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 voltage. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40985 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 2 duration.
40986 | V2 | V2 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 2 voltage.
40987 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 3 duration.
40988 | V3 | V3 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 3 voltage.
40989 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 4 duration.
40990 | V4 | V4 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 4 voltage.
40991 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 5 duration.
40992 | V5 | V5 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 5 voltage.
40993 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 6 duration.
40994 | V6 | V6 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 6 voltage.
40995 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 duration.
40996 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 voltage.
40997 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 duration.
40998 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 voltage.
40999 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 duration.
41000 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 voltage.
41001 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 duration.
41002 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 voltage.
41003 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 duration.
41004 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 voltage.
41005 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 duration.
41006 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 voltage.
41007 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 duration.
41008 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 voltage.
41009 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 duration.
41010 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 voltage.
41011 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 duration.
41012 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 voltage.
41013 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 duration.
41014 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 voltage.
41015 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 duration.
41016 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 voltage.
41017 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 duration.
41018 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 voltage.
41019 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 duration.
41020 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 voltage.
41021 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 duration.
41022 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 voltage.
41023 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
41031 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 140
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
41032 | ID | HVRTX |  | uint16 |  |  | 140 |  |  | HVRT extended curve
41033 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
41034 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve.
41035 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | Bit 0 | 1 = ENABLED |  |  | The enable of HVRT is shared with LVRT so setting this bit has the same effect on "ModEna" register of M139.
41036 | WinTms | WinTms |  | uint16 | Secs |  | unimplemented |  | RW | Time window for LVRT change.
41037 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for LVRT curve selection.
41038 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
41039 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
41040 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximumn of 20).
41041 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
41042 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
41043 | CrvType |  |  | enum16 |  |  | supported |  | R
[7 empty] | 1 | CEASE_TO_ENERGIZE
41044 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
41045 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 1 duration.
41046 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 voltage. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
41047 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 2 duration.
41048 | V2 | V2 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 2 voltage.
41049 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 3 duration.
41050 | V3 | V3 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 3 voltage.
41051 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 4 duration.
41052 | V4 | V4 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 4 voltage.
41053 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 5 duration.
41054 | V5 | V5 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 5 voltage.
41055 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 6 duration.
41056 | V6 | V6 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 6 voltage.
41057 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 duration.
41058 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 voltage.
41059 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 duration.
41060 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 voltage.
41061 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 duration.
41062 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 voltage.
41063 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 duration.
41064 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 voltage.
41065 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 duration.
41066 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 voltage.
41067 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 duration.
41068 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 voltage.
41069 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 duration.
41070 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 voltage.
41071 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 duration.
41072 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 voltage.
41073 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 duration.
41074 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 voltage.
41075 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 duration.
41076 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 voltage.
41077 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 duration.
41078 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 voltage.
41079 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 duration.
41080 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 voltage.
41081 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 duration.
41082 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 voltage.
41083 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 duration.
41084 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 voltage.
41085 | CrvNam | CrvNam | 1 | string |  |  | supported |  | RW | Optional description for curve.
41093 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 145
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
41094 | ID | Extended Settings |  | uint16 |  |  | 145 |  |  | Inverter controls extended settings
41095 | L | [5 empty] | 8 |  |  | Model Length
41096 | NomRmpUpRte | Ramp Up Rate |  | uint16 | Pct | Rmp_SF | supported |  | RW | Ramp up rate as a percentage of max current. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
41097 | NomRmpDnRte | NomRmpDnRte |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Ramp down rate as a percentage of max current.
41098 | EmgRmpUpRte | Emergency Ramp Up Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Emergency ramp down rate as a percentage of max current.
41099 | EmgRmpDnRte | Emergency Ramp Down Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Emergency ramp down rate as a percentage of max current.
41100 | ConnRmpUpRte | Connect Ramp Up Rate |  | uint16 | Pct | Rmp_SF | supported |  | RW | Connect ramp up rate as a percentage of max current. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
41101 | ConnRmpDnRte | Connect Ramp Down Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Connect ramp down rate as a percentage of max current.
41102 | AGra | Default Ramp Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Ramp rate specified in percent of max current.
41103 | Rmp_SF | Ramp Rate Scale Factor |  | sunssf |  |  | -1 |  | R | Ramp Rate Scale Factor

## 160
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Conformance Notes
41104 | ID | Multiple MPPT Inverter Extension Model |  | uint16 |  |  | 160 |  |  | Configuration of MPPT channels: Target product supports vendor-specific configuration of MPPT channels, also known as "input mode". The following configuration modes are supported: - Independent MPPT: A separate MPPT control runs on each channel so state conditions (e.g. "DCSt" register on M160 repeating blocks) are independent. - Parallel MPPT: Channel are connected in parallel to the same source and a unique MPPT control runs for all of them so many state conditions (e.g. "DCSt" register on M160 repeating blocks) are redundant.
41105 | L |  |  | uint16 |  |  | 128
41106 | DCA_SF | Current Scale Factor |  | sunssf |  |  | -1 |  | R
41107 | DCV_SF | Voltage Scale Factor |  | sunssf |  |  | -1 |  | R
41108 | DCW_SF | Power Scale Factor |  | sunssf |  |  | 1 |  | R
41109 | DCWH_SF | Energy Scale Factor |  | sunssf |  |  | unimplemented |  | R
41110 | Evt | Global Events |  | bitfield32 |  |  | supported |  | R
[7 empty] | Bit 0 | 1 =Ground Fault (GROUND_FAULT) |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 =Input Over Voltage (INPUT_OVER_VOLTAGE) |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | Reserved (RESERVED)
[7 empty] | unimplemented | DC Disconnect (DC_DISCONNECT)
[7 empty] | unimplemented | Cabinet Open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 =Manual Shutdown (MANUAL_SHUTDOWN) |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 =Over Temperature (OVER_TEMP) |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | unimplemented | Blown Fuse (BLOWN_FUSE)
[7 empty] | Bit 13 | 1 = Under Temperature (UNDER_TEMP) |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | Bit 14 | 1 = Memory Loss (MEMORY_LOSS) |  | This state corresponds to statistics memory fault.
[7 empty] | Bit 15 | 1 = Arc Detection (ARC_DETECTION) |  | This state corresponds to the following internal alarms: - E050: Arc-Fault
[7 empty] | Bit 20 | 1 = Test Failed (TEST_FAILED) |  | This state corresponds to the following internal alarms: - E005: Internal bus fault - E013: Wrong DC input mode - E019: Lekage current self-test fault - E020: Grid interface self-test fault - E021: Grid interface self-test fault - E053: Arc-fault detector self-test fault - E078: R-iso self-test fault
[7 empty] | Bit 21 | 1 = Under Voltage (INPUT_UNDER_VOLTAGE) |  | This state corresponds to the following internal alarms: - W002: Input UV
[7 empty] | Bit 22 | 1 = Over Current (INPUT_OVER_CURRENT) |  | This state corresponds to the following internal alarms: - E001: Input OC
41112 | N | Number of Modules |  | count |  |  | supported |  | R
41113 | TmsPer | Timestamp Period |  | uint16 |  |  | unimplemented |  | R
41114 | ID | Input ID | 1 | uint16 |  |  | supported |  | R
41115 | IDStr | Input ID Sting | 1 | string |  |  | supported |  | R
41123 | DCA | DC Current | 1 | uint16 | A | DCA_SF | supported |  | R
41124 | DCV | DC Voltage | 1 | uint16 | V | DCV_SF | supported |  | R
41125 | DCW | DC Power | 1 | uint16 | W | DCW_SF | supported |  | R
41126 | DCWH | Lifetime Energy | 1 | acc32 | Wh | DCWH_SF | unimplemented |  | R
41128 | Tms | Timestamp | 1 | uint32 | Secs |  | unimplemented |  | R
41130 | Tmp | Temperature | 1 | int16 | C |  | unimplemented |  | R
41131 | DCSt | Operating State | 1 | enum16 |  |  | supported |  | R
[7 empty] | 1 | Off (OFF) |  | This state corresponds to unloaded/disconnected DC channel.
[7 empty] | 2 | Sleeping (SLEEPING) |  | This state corresponds to connected DC channel but not ready for starting MPPT (e.g. for low voltage condition).
[7 empty] | 3 | Starting (STARTING) |  | This state corresponds to connected DC channel starting MPPT regulation.
[7 empty] | 4 | MPPT |  | This state corresponds to connected DC channel running MPPT regulation.
[7 empty] | 5 | Throttled (THROTTLED) |  | This state corresponds to connected DC channel with forced MPPT suspension (e,g, for by-pass or power-saving purposes).
[7 empty] | unimplemented | Shutting Down (SHUTTING_DOWN)
[7 empty] | 7 | Fault (FAULT) |  | This state corresponds to connected DC channel with pending fault (under-voltage, over-voltage, over-current).
[7 empty] | unimplemented | Standby (STANDBY)
[7 empty] | unimplemented | Test (TEST)
[7 empty] | unimplemented | Reserved (RESERVED)
41132 | DCEvt | Module Events | 1 | bitfield32 |  |  | supported |  | R
[7 empty] | Bit 0 | 1 =Ground Fault (GROUND_FAULT) |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 =Input Over Voltage (INPUT_OVER_VOLTAGE) |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | Reserved (RESERVED)
[7 empty] | unimplemented | DC Disconnect (DC_DISCONNECT)
[7 empty] | unimplemented | Cabinet Open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 =Manual Shutdown (MANUAL_SHUTDOWN) |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 =Over Temperature (OVER_TEMP) |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | unimplemented | Blown Fuse (BLOWN_FUSE)
[7 empty] | Bit 13 | 1 = Under Temperature (UNDER_TEMP) |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | Bit 14 | 1 = Memory Loss (MEMORY_LOSS) |  | This state corresponds to statistics memory fault.
[7 empty] | Bit 15 | 1 = Arc Detection (ARC_DETECTION) |  | This state corresponds to the following internal alarms: - E050: Arc-Fault
[7 empty] | Bit 20 | 1 = Test Failed (TEST_FAILED) |  | This state corresponds to the following internal alarms: - E005: Internal bus fault - E013: Wrong DC input mode - E019: Lekage current self-test fault - E020: Grid interface self-test fault - E021: Grid interface self-test fault - E053: Arc-fault detector self-test fault - E078: R-iso self-test fault
[7 empty] | Bit 21 | 1 = Under Voltage (INPUT_UNDER_VOLTAGE) |  | This state corresponds to the following internal alarms: - W002: Input UV
[7 empty] | Bit 22 | 1 = Over Current (INPUT_OVER_CURRENT) |  | This state corresponds to the following internal alarms: - E001: Input OC
41134 | ID | Input ID | 2 | uint16 |  |  | supported |  | R
41135 | IDStr | Input ID Sting | 2 | string |  |  | supported |  | R
41143 | DCA | DC Current | 2 | uint16 | A | DCA_SF | supported |  | R
41144 | DCV | DC Voltage | 2 | uint16 | V | DCV_SF | supported |  | R
41145 | DCW | DC Power | 2 | uint16 | W | DCW_SF | supported |  | R
41146 | DCWH | Lifetime Energy | 2 | acc32 | Wh | DCWH_SF | unimplemented |  | R
41148 | Tms | Timestamp | 2 | uint32 | Secs |  | unimplemented |  | R
41150 | Tmp | Temperature | 2 | int16 | C |  | unimplemented |  | R
41151 | DCSt | Operating State | 2 | enum16 |  |  | supported |  | R
41152 | DCEvt | Module Events | 2 | bitfield32 |  |  | supported |  | R
41154 | ID | Input ID | 3 | uint16 |  |  | supported |  | R
41155 | IDStr | Input ID Sting | 3 | string |  |  | supported |  | R
41163 | DCA | DC Current | 3 | uint16 | A | DCA_SF | supported |  | R
41164 | DCV | DC Voltage | 3 | uint16 | V | DCV_SF | supported |  | R
41165 | DCW | DC Power | 3 | uint16 | W | DCW_SF | supported |  | R
41166 | DCWH | Lifetime Energy | 3 | acc32 | Wh | DCWH_SF | unimplemented |  | R
41168 | Tms | Timestamp | 3 | uint32 | Secs |  | unimplemented |  | R
41170 | Tmp | Temperature | 3 | int16 | C |  | unimplemented |  | R
41171 | DCSt | Operating State | 3 | enum16 |  |  | supported |  | R
41172 | DCEvt | Module Events | 3 | bitfield32 |  |  | supported |  | R
41174 | ID | Input ID | 4 | uint16 |  |  | supported |  | R
41175 | IDStr | Input ID Sting | 4 | string |  |  | supported |  | R
41183 | DCA | DC Current | 4 | uint16 | A | DCA_SF | supported |  | R
41184 | DCV | DC Voltage | 4 | uint16 | V | DCV_SF | supported |  | R
41185 | DCW | DC Power | 4 | uint16 | W | DCW_SF | supported |  | R
41186 | DCWH | Lifetime Energy | 4 | acc32 | Wh | DCWH_SF | unimplemented |  | R
41188 | Tms | Timestamp | 4 | uint32 | Secs |  | unimplemented |  | R
41190 | Tmp | Temperature | 4 | int16 | C |  | unimplemented |  | R
41191 | DCSt | Operating State | 4 | enum16 |  |  | supported |  | R
41192 | DCEvt | Module Events | 4 | bitfield32 |  |  | supported |  | R
41194 | ID | Input ID | 5 | uint16 |  |  | supported |  | R
41195 | IDStr | Input ID Sting | 5 | string |  |  | supported |  | R
41203 | DCA | DC Current | 5 | uint16 | A | DCA_SF | supported |  | R
41204 | DCV | DC Voltage | 5 | uint16 | V | DCV_SF | supported |  | R
41205 | DCW | DC Power | 5 | uint16 | W | DCW_SF | supported |  | R
41206 | DCWH | Lifetime Energy | 5 | acc32 | Wh | DCWH_SF | unimplemented |  | R
41208 | Tms | Timestamp | 5 | uint32 | Secs |  | unimplemented |  | R
41210 | Tmp | Temperature | 5 | int16 | C |  | unimplemented |  | R
41211 | DCSt | Operating State | 5 | enum16 |  |  | supported |  | R
41212 | DCEvt | Module Events | 5 | bitfield32 |  |  | supported |  | R
41214 | ID | Input ID | 6 | uint16 |  |  | supported |  | R
41215 | IDStr | Input ID Sting | 6 | string |  |  | supported |  | R
41223 | DCA | DC Current | 6 | uint16 | A | DCA_SF | supported |  | R
41224 | DCV | DC Voltage | 6 | uint16 | V | DCV_SF | supported |  | R
41225 | DCW | DC Power | 6 | uint16 | W | DCW_SF | supported |  | R
41226 | DCWH | Lifetime Energy | 6 | acc32 | Wh | DCWH_SF | unimplemented |  | R
41228 | Tms | Timestamp | 6 | uint32 | Secs |  | unimplemented |  | R
41230 | Tmp | Temperature | 6 | int16 | C |  | unimplemented |  | R
41231 | DCSt | Operating State | 6 | enum16 |  |  | supported |  | R
41232 | DCEvt | Module Events | 6 | bitfield32 |  |  | supported |  | R

## 403
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
41234 | ID | String Combiner (Current) |  | uint16 |  |  | 403 |  |  | A basic string combiner model
41235 | L |  |  | uint16 |  |  | 208 |  |  | Model Length
41236 | DCA_SF |  |  | sunssf |  |  | -1 |  | R | Current scale factor
41237 | DCAhr_SF |  |  | sunssf |  |  | unimplemented |  | R | Amp-hour scale factor
41238 | DCV_SF |  |  | sunssf |  |  | unimplemented |  | R | Voltage scale factor
41239 | DCAMax | Rating |  | uint16 | A | DCA_SF | supported |  | R | Maximum DC Current Rating
41240 | N | N |  | count |  |  | supported |  | R | Number of Inputs
41241 | Evt | Event |  | bitfield32 |  |  | supported |  | R | Bitmask value. Events
[7 empty] | unimplemented | LOW_VOLTAGE
[7 empty] | unimplemented | LOW_POWER
[7 empty] | unimplemented | LOW_EFFICIENCY
[7 empty] | Bit 3 | 1 = CURRENT
[7 empty] | unimplemented | VOLTAGE
[7 empty] | unimplemented | POWER
[7 empty] | unimplemented | PR
[7 empty] | Bit 7 | 1 = DISCONNECTED
[7 empty] | Bit 8 | 1 = FUSE_FAULT
[7 empty] | unimplemented | COMBINER_FUSE_FAULT
[7 empty] | unimplemented | COMBINER_CABINET_OPEN
[7 empty] | unimplemented | TEMP
[7 empty] | unimplemented | GROUNDFAULT
[7 empty] | unimplemented | REVERSED_POLARITY
[7 empty] | unimplemented | INCOMPATIBLE
[7 empty] | unimplemented | COMM_ERROR
[7 empty] | unimplemented | INTERNAL_ERROR
[7 empty] | unimplemented | THEFT
[7 empty] | unimplemented | ARC_DETECTED
41243 | EvtVnd | Vendor Event |  | bitfield32 |  |  | unimplemented |  | R | Bitmask value. Vendor defnied events
41245 | DCA | Amps |  | int16 | A | DCA_SF | supported |  | R | Total measured current
41246 | DCAhr | Amp-hours |  | acc32 | Ah | DCAhr_SF | unimplemented |  | R | Total metered Amp-hours
41248 | DCV | Voltage |  | int16 | V | DCV_SF | unimplemented |  | R | Output Voltage
41249 | Tmp | Temp |  | int16 | C |  | supported |  | R | Internal operating temperature
41250 | InDCA_SF |  |  | sunssf |  |  | -1 |  | R | Current scale factor for inputs
41251 | InDCAhr_SF |  |  | sunssf |  |  | unimplemented |  | R | Amp-hour scale factor for inputs
41252 | InID | ID | 1 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41253 | InEvt | Event | 1 | bitfield32 |  |  | supported |  | R | String Input Event Flags
[7 empty] | unimplemented | LOW_VOLTAGE
[7 empty] | unimplemented | LOW_POWER
[7 empty] | unimplemented | LOW_EFFICIENCY
[7 empty] | Bit 3 | 1 = CURRENT
[7 empty] | unimplemented | VOLTAGE
[7 empty] | unimplemented | POWER
[7 empty] | unimplemented | PR
[7 empty] | Bit 7 | 1 = DISCONNECTED
[7 empty] | Bit 8 | 1 = FUSE_FAULT
[7 empty] | unimplemented | COMBINER_FUSE_FAULT
[7 empty] | unimplemented | COMBINER_CABINET_OPEN
[7 empty] | unimplemented | TEMP
[7 empty] | unimplemented | GROUNDFAULT
[7 empty] | unimplemented | REVERSED_POLARITY
[7 empty] | unimplemented | INCOMPATIBLE
[7 empty] | unimplemented | COMM_ERROR
[7 empty] | unimplemented | INTERNAL_ERROR
[7 empty] | unimplemented | THEFT
[7 empty] | unimplemented | ARC_DETECTED
41255 | InEvtVnd | Vendor Event | 1 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41257 | InDCA | Amps | 1 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41258 | InDCAhr | Amp-hours | 1 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41260 | InID | ID | 2 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41261 | InEvt | Event | 2 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41263 | InEvtVnd | Vendor Event | 2 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41265 | InDCA | Amps | 2 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41266 | InDCAhr | Amp-hours | 2 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41268 | InID | ID | 3 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41269 | InEvt | Event | 3 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41271 | InEvtVnd | Vendor Event | 3 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41273 | InDCA | Amps | 3 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41274 | InDCAhr | Amp-hours | 3 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41276 | InID | ID | 4 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41277 | InEvt | Event | 4 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41279 | InEvtVnd | Vendor Event | 4 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41281 | InDCA | Amps | 4 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41282 | InDCAhr | Amp-hours | 4 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41284 | InID | ID | 5 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41285 | InEvt | Event | 5 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41287 | InEvtVnd | Vendor Event | 5 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41289 | InDCA | Amps | 5 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41290 | InDCAhr | Amp-hours | 5 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41292 | InID | ID | 6 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41293 | InEvt | Event | 6 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41295 | InEvtVnd | Vendor Event | 6 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41297 | InDCA | Amps | 6 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41298 | InDCAhr | Amp-hours | 6 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41300 | InID | ID | 7 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41301 | InEvt | Event | 7 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41303 | InEvtVnd | Vendor Event | 7 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41305 | InDCA | Amps | 7 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41306 | InDCAhr | Amp-hours | 7 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41308 | InID | ID | 8 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41309 | InEvt | Event | 8 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41311 | InEvtVnd | Vendor Event | 8 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41313 | InDCA | Amps | 8 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41314 | InDCAhr | Amp-hours | 8 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41316 | InID | ID | 9 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41317 | InEvt | Event | 9 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41319 | InEvtVnd | Vendor Event | 9 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41321 | InDCA | Amps | 9 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41322 | InDCAhr | Amp-hours | 9 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41324 | InID | ID | 10 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41325 | InEvt | Event | 10 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41327 | InEvtVnd | Vendor Event | 10 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41329 | InDCA | Amps | 10 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41330 | InDCAhr | Amp-hours | 10 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41332 | InID | ID | 11 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41333 | InEvt | Event | 11 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41335 | InEvtVnd | Vendor Event | 11 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41337 | InDCA | Amps | 11 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41338 | InDCAhr | Amp-hours | 11 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41340 | InID | ID | 12 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41341 | InEvt | Event | 12 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41343 | InEvtVnd | Vendor Event | 12 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41345 | InDCA | Amps | 12 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41346 | InDCAhr | Amp-hours | 12 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41348 | InID | ID | 13 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41349 | InEvt | Event | 13 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41351 | InEvtVnd | Vendor Event | 13 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41353 | InDCA | Amps | 13 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41354 | InDCAhr | Amp-hours | 13 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41356 | InID | ID | 14 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41357 | InEvt | Event | 14 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41359 | InEvtVnd | Vendor Event | 14 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41361 | InDCA | Amps | 14 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41362 | InDCAhr | Amp-hours | 14 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41364 | InID | ID | 15 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41365 | InEvt | Event | 15 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41367 | InEvtVnd | Vendor Event | 15 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41369 | InDCA | Amps | 15 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41370 | InDCAhr | Amp-hours | 15 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41372 | InID | ID | 16 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41373 | InEvt | Event | 16 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41375 | InEvtVnd | Vendor Event | 16 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41377 | InDCA | Amps | 16 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41378 | InDCAhr | Amp-hours | 16 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41380 | InID | ID | 17 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41381 | InEvt | Event | 17 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41383 | InEvtVnd | Vendor Event | 17 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41385 | InDCA | Amps | 17 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41386 | InDCAhr | Amp-hours | 17 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41388 | InID | ID | 18 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41389 | InEvt | Event | 18 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41391 | InEvtVnd | Vendor Event | 18 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41393 | InDCA | Amps | 18 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41394 | InDCAhr | Amp-hours | 18 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41396 | InID | ID | 19 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41397 | InEvt | Event | 19 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41399 | InEvtVnd | Vendor Event | 19 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41401 | InDCA | Amps | 19 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41402 | InDCAhr | Amp-hours | 19 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41404 | InID | ID | 20 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41405 | InEvt | Event | 20 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41407 | InEvtVnd | Vendor Event | 20 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41409 | InDCA | Amps | 20 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41410 | InDCAhr | Amp-hours | 20 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41412 | InID | ID | 21 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41413 | InEvt | Event | 21 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41415 | InEvtVnd | Vendor Event | 21 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41417 | InDCA | Amps | 21 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41418 | InDCAhr | Amp-hours | 21 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41420 | InID | ID | 22 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41421 | InEvt | Event | 22 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41423 | InEvtVnd | Vendor Event | 22 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41425 | InDCA | Amps | 22 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41426 | InDCAhr | Amp-hours | 22 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41428 | InID | ID | 23 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41429 | InEvt | Event | 23 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41431 | InEvtVnd | Vendor Event | 23 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41433 | InDCA | Amps | 23 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41434 | InDCAhr | Amp-hours | 23 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours
41436 | InID | ID | 24 | uint16 |  |  | supported |  | R | Uniquely identifies this input set
41437 | InEvt | Event | 24 | bitfield32 |  |  | supported |  | R | String Input Event Flags
41439 | InEvtVnd | Vendor Event | 24 | bitfield32 |  |  | unimplemented |  | R | String Input Vendor Event Flags
41441 | InDCA | Amps | 24 | int16 | A | InDCA_SF | supported |  | R | String Input Current
41442 | InDCAhr | Amp-hours | 24 | acc32 | Ah | InDCAhr_SF | unimplemented |  | R | String Input Amp-Hours

## 65230
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Conformance Notes
41444 | ID | [5 empty] | 65230
41445 | L | [5 empty] | 1
41446 | LatchRest_Ena |  |  | enum16 |  |  | supported |  | RW | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. Write register to 1 (ENABLED) for removing a latch condition; immediately after, register is automatically set to 0.

## 65232
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Conformance Notes
41447 | ID | Additional Functions |  | uint16 |  |  | 65232 |  | R | Additional Functions vendor model (available only for the B2 version product family)
41448 | L |  |  | uint16 |  |  | 20 |  | R | Model Length
41449 | GNDKit _Inst | Gounding kit |  | enum16 |  |  | supported |  | R | Presence of Grounding kit. The activation of the board must be done through Web User Interface
[7 empty] | 0 | NOT INSTALLED
[7 empty] | 1 | INSTALLED
41450 | RSDBleed_Inst | Rapid Shut Down Compatibility Kit |  | enum16 |  |  | supported |  | R | Presence of Rapid Shut Down Compatibility Kit.
[7 empty] | 0 | NOT INSTALLED
[7 empty] | 1 | INSTALLED
41451 | QNT_Inst | Pre-Charge Kit |  | enum16 |  |  | supported |  | R | Presence of PreCharge kit The activation of the board must be done through Web User Interface
[7 empty] | 0 | NOT INSTALLED
[7 empty] | 1 | INSTALLED
41452 | PID _Inst | Anti-PID Kit |  | enum16 |  |  | supported |  | R | Presence of Anti-PID kit The activation of the board must be done through Web User Interface
[7 empty] | 0 | NOT INSTALLED
[7 empty] | 1 | INSTALLED
41453 | Vneg_GND | Vneg-gnd |  | uint16 | V | VGND_SF | supported |  | R | Measured Voltage between DC Negative Pole and Ground
41454 | Vpos_GND | Vpos-gnd |  | uint16 | V | VGND_SF | supported |  | R | Measured Voltage between DC Positive Pole and Ground
41455 | Night_Mod_State | Night Reactive Power Status |  | enum16 |  |  | supported |  | R | Current Time status for Reactive Power Mode, during night time the Night Reactive Power Mode is applied
[7 empty] | 0 | DAY TIME
[7 empty] | 1 | NIGHT TIME
41456 | DS_Ena | Energy Save Mode |  | enum16 |  |  | supported |  | RW | Energy Save mode enabler. When the inverter is in Energy Save mode the night consumption will be reduced and measures will not be available during night time
41457 | Night_Mod | Night Reactive Power Mode |  | enum16 |  |  | supported |  | RW | Settings for Night Reactive Power Mode. In case of Reactive Power is suggested to use the reactive power set point on model 123 for Plant Control purpose. Night TIme Reactive Power is mutually exclusive with Anti-PID mode, when Anti-PID mode is enabled the Night Reactive Power will be automatically disabled and vice-versa
[7 empty] | 0 | DISABLED
[7 empty] | 1 | REACTIVE POWER
[7 empty] | 2 | VOLT-VAR REACTIVE_POWER
41458 | QFixVArMaxPct | Night Q Fix Set-Point |  | int16 | % VAMax or % WMax or % VArMax | NightQFix_SF | supported |  | RW | Fixed Reactive Power compensation during Night Time, for dynamic behavior with a Plant Control it is mandatory to use the reactive power set point on data model 123. The set Point can be espressed as % of % VAMax, % WMax or % VArMax according to the reactive power mode VArPct_Mod available data model 123 - Immediate Control
41459 | Anti_PID_State | Anti-PID Status |  | enum16 |  |  | supported |  | R | Anti-PID mode running info, the Anti-PID function will be running when activated during night time
[7 empty] | 0 | NOT RUNNING
[7 empty] | 1 | RUNNING
41460 | Anti_PID_Mod | Anti-PID Mode |  | enum16 |  |  | supported |  | RW | Anti-PID mode enabler. Anti-PID is mutually exclusive with Night Reactive Power mode, when Anti-PID mode is enabled the Night Reactive Power will be automatically disabled and vice-versa
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
41461 | PID_VRef | Anti-PID Reference Voltage |  | enum16 |  |  | supported |  | RW | Inverter will apply an Anti-PID Reference Voltage to the PV panels when the Anti-PID function is running. NOTE: Anti-PID Lock out voltage + Anti-PID Reference Voltage MUST be below 1500VDc and the inverter will not allow any change that are not compatible with this constraint
[7 empty] | 0 | 500V
[7 empty] | 1 | 650V
[7 empty] | 2 | 800V
41462 | PID_Thr | Anti-PID Lock-In/Out Voltage |  | enum16 |  |  | supported |  | RW | Lock In Voltage (first value) defines when the Anti-PID function will be activacted. At night, when the DC voltage drop down continuouly below the Anti-PID Lock In Voltage for a time greater than PID_Delay the inverter activates the Anti-PID function and will provide the reference voltage to the PV Panels. Lock Out Voltage (second value) is always equal to the Lock In Voltage + 10%Min Vstart and defines when the Anti-PID function will be deactivacted. At morning, when the DC Voltage increase above the Anti-PID Lock Out Voltage the inverter deactivates the Anti-PID function and will start to convert the DC power into the grid. MinVstart is the minimum Starting Voltage between all the MPPTs. NOTE: Anti-PID Lock out voltage + Anti-PID Reference Voltage MUST be below 1500VDc and the inverter will not allow any change that are not compatible with this constraint
[7 empty] | 0 | 10%MinVstart / 20%MinVstart
[7 empty] | 1 | 20%MinVstart / 30%MinVstart
[7 empty] | 2 | 30%MinVstart / 40%MinVstart
[7 empty] | 3 | 40%MinVstart / 50% MinVstart
41463 | PID_Delay | Anti-PID Starting Delay |  | uint16 | min |  | supported |  | RW | Time windows used to assure that the voltage is steadily below the Anti-PID Lock In Voltage. Inverter activate the Anti-PID function only when the DC voltage drop down continuouly below the Anti-PID Lock In Voltage for a time greater than PID_Delay
41464 | VGND_SF |  |  | sunssf |  |  | supported |  | R | Scale Factor for Pole to Ground measures
41465 | NightQFix_SF |  |  | sunssf |  |  | supported |  | R | Scale factor for Fixed Reactive Power Set Point
41466 | Reserved | [8 empty] | Reserved for future scope
41467 | Reserved | [8 empty] | Reserved for future scope
41468 | Reserved | [8 empty] | Reserved for future scope