## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.4a based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
NOTE (SunSpec model 101/103): This PICS applies to both single-phase and three-phase inverter. Ensure you use the model corresponding to your device, SunSpec Model 101 for single-phase or SunSpec Model 103 for three-phase systems, i.e.: a) PowerUNO series (Single-phase): Use SunSpec Model 101 b) PowerTRIO series (Three-phase): Use SunSpec Model 103
Important Note on Dynamic Register Addressing SunSpec models utilize a modular structure that may include Repeated Blocks as a function of number of Meters, MPPTs and batteries. Because the length of these models depends on the number of active blocks, the starting address of all subsequent models is dynamic. Implementation Guideline: To ensure correct integration, the user must not rely on fixed absolute addresses. Instead, the software should dynamically discover the starting address of each model by: 1) Reading the Model_ID_address and the Length_value field of the current model. 2) Calculating the address of the next model as: Next_model_start_address = Current_model_start_address + Length + 2

## Certification Info
Certificate Number | ----
Date | 2026-04-24 11:37
Manufacturer Name | FIMER
Product Name | PowerUNO and PowerTRIO series
Product Models | FIM-HY-2.0/3.0/3.3/3.6/4.0/4.6/5.0/6.0-SE-A-1PH FIM-HY-4.0/5.0/6.0/7.5/8.0/8.5/10.0-SE-A-3PH
Product Description | Single/Three Phase String hybrid Inverter

## Versioning
Version | Change Log | Date of Change | Min. Ref. FW version Inverter
0 | - First version - | 2026-04-24 | 2615A
1 | Models 101 and 103: Filled in missing 'name' values. Model 65234: Fixed an incorrect register and added missing entries for the second battery. | 2026-04-30 | 2615A

## 1
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40002 | ID | Common |  | uint16 |  |  | 1 |  |  | All SunSpec compliant devices must include this as the first model
40003 | L |  |  | uint16 |  |  | 66 |  |  | Model Length
40004 | Mn | Manufacturer |  | string |  |  | FIMER |  | R | Well known value registered with SunSpec for compliance
40020 | Md | Model |  | string |  |  | FIM-HY-8.5-3PH |  | R | Manufacturer specific value (32 chars) | Provided Md string
40036 | Opt | Options |  | string |  |  | 4105 2018_rev1 |  | R | Manufacturer specific value (16 chars) | Provided Grid Standard currently applied by the inverter
40044 | Vr | Version |  | string |  |  | 2615A |  | R | Manufacturer specific value (16 chars) | Provided SW release version string is formatted as [Y + WY + DW] where Y is the release year (format YY), WY is the release week of the year (format WW) and DW is the release day of the week (encoded as a single ASCII character starting from 'A' which is associated to Monday) Example: 1801C is the encoding number that define the firmware released Wednesday on the first week of 2018
40052 | Number | Serial |  | string |  |  | 2442101138 |  | R | Manufacturer specific value (32 chars) | Provided official serial number string formatted as [YW+SN] where SN is the internal serial number of the unit, and YW is the manufacturing year/weak date expressed in YYWW format.
40068 | Address | Device |  | uint16 |  |  | 1 |  | R | Modbus device address
40069 | Pad | Pad |  | pad |  |  |  |  | R | Force even alignment

## 101
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40070 | ID | Inverter (Single Phase) |  | uint16 |  |  | 103 |  |  | Include this model for single phase inverter monitoring
40071 | L |  |  | uint16 |  |  | 50 |  |  | Model Length
40072 | A | Amps |  | uint16 | A | A_SF | supported |  | R | AC Current
40073 | AphA | Amps PhaseA |  | uint16 | A | A_SF | supported |  | R | Phase A Current
40074 | AphB | Amps PhaseB |  | uint16 | A | A_SF | unimplemented |  | R | Phase B Current
40075 | AphC | Amps PhaseC |  | uint16 | A | A_SF | unimplemented |  | R | Phase C Current
40076 | A_SF | A_SF |  | sunssf |  |  | -1 |  | R
40077 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | unimplemented |  | R | Phase Voltage AB
40078 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | unimplemented |  | R | Phase Voltage BC
40079 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | unimplemented |  | R | Phase Voltage CA
40080 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | supported |  | R | Phase Voltage AN
40081 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | unimplemented |  | R | Phase Voltage BN
40082 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | unimplemented |  | R | Phase Voltage CN
40083 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R
40084 | W | Watts |  | int16 | W | W_SF | supported |  | R | AC Power
40085 | W_SF | W_SF |  | sunssf |  |  | 1 |  | R
40086 | Hz | Hz |  | uint16 | Hz | Hz_SF | supported |  | R | Line Frequency
40087 | Hz_SF | Hz_SF |  | sunssf |  |  | -2 |  | R
40088 | VA | VA |  | int16 | VA | VA_SF | supported |  | R | AC Apparent Power
40089 | VA_SF | VA_SF |  | sunssf |  |  | 1 |  | R
40090 | Var | Var |  | int16 | var | VAr_SF | supported |  | R | AC Reactive Power
40091 | VAr_SF | VAr_SF |  | sunssf |  |  | 1 |  | R
40092 | PF | PF |  | int16 | Pct | PF_SF | supported |  | R | AC Power Factor | Default: EEI
40093 | PF_SF | PF_SF |  | sunssf |  |  | -4 |  | R
40094 | WH | WattHours |  | acc32 | Wh | WH_SF | supported |  | R | AC Energy | Total Energy is provided on model 122 (ActWh)
40096 | WH_SF | WH_SF |  | sunssf |  |  | 1 |  | R
40097 | DCA | DC Amps |  | uint16 | A | DCA_SF | supported |  | R | DC Current
40098 | DCA_SF | DCA_SF |  | sunssf |  |  | -1 |  | R
40099 | DCV | DC Voltage |  | uint16 | V | DCV_SF | unimplemented |  | R | DC Voltage | For this product the DC voltage is not provided with model 103 but using model 160.
40100 | DCV_SF | DCV_SF |  | sunssf |  |  | unimplemented |  | R
40101 | DCW | DC Watts |  | int16 | W | DCW_SF | supported |  | R | DC Power
40102 | DCW_SF | DCW_SF |  | sunssf |  |  | 1 |  | R
40103 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | supported |  | R | Cabinet Temperature | This measure is implemented as logic board temperature.
40104 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | supported |  | R | Heat Sink Temperature | This measure is implemented as DC/AC (inverter) stage temperature.
40105 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | unimplemented |  | R | Transformer Temperature
40106 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | supported |  | R | Other Temperature | This measure is implemented as DC/DC (inverter) stage temperature.
40107 | Tmp_SF | Tmp_SF |  | sunssf |  |  | -1 |  | R
40108 | St | Operating State |  | enum16 |  |  | supported |  | R | Enumerated value. Operating state
[7 empty] | 1 | Off (OFF) |  |  | This state corresponds to startup phase of inverter controller.
[7 empty] | 2 | Sleeping (SLEEPING) |  |  | This state corresponds to execution of grid interface "auto-test" required by Italian country standard.
[7 empty] | 3 | Starting (STARTING) |  |  | This state corresponds to grid connection phase.
[7 empty] | 4 | MPPT |  |  | This state corresponds to inverter connected to grid and running with MPPT.
[7 empty] | 5 | Throttled (THROTTLED) |  |  | This state corresponds to inverter connected to grid and running with limited active power (derating).
[7 empty] | 6 | Shutting down (SHUTTING_DOWN) |  |  | This state corresponds to forced disconnection from grid (e.g. commanded by user through "remote off" command).
[7 empty] | 7 | Fault (FAULT) |  |  | This state corresponds to fault causing disconnection from grid.
[7 empty] | 8 | Standby (STANDBY) |  |  | This state corresponds to disconnection from grid caused by missing DC source or AC grid.
40109 | StVnd | Vendor Operating State |  | enum16 |  |  | supported |  | R | Vendor specific operating state code
40110 | Evt1 | Event1 |  | bitfield32 |  |  | supported |  | R | Bitmask value. Event fields
[7 empty] | Bit 0 | 1 = Ground fault (GROUND_FAULT) |  |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 = DC over voltage (DC_OVER_VOLT) |  |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | AC disconnect open (AC_DISCONNECT)
[7 empty] | unimplemented | DC disconnect open (DC_DISCONNECT)
[7 empty] | Bit 4 | 1 = Grid shutdown (GRID_DISCONNECT) |  |  | This state corresponds to grid absence.
[7 empty] | unimplemented | Cabinet open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 = Manual shutdown (MANUAL_SHUTDOWN) |  |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 = Over temperature (OVER_TEMP) |  |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | Bit 8 | 1 = Frequency above limit (OVER_FREQUENCY) |  |  | This state corresponds to the following internal alarms: - E006: Grid OF
[7 empty] | Bit 9 | 1 = Frequency under limit (UNDER_FREQUENCY) |  |  | This state corresponds to the following internal alarms: - E007: Grid UF
[7 empty] | Bit 10 | 1 = AC Voltage above limit (AC_OVER_VOLT) |  |  | This state corresponds to the following internal alarms: - E003: Grid OV
[7 empty] | Bit 11 | 1 = AC Voltage under limit (AC_UNDER_VOLT) |  |  | This state corresponds to the following internal alarms: - E004: Grid UV
[7 empty] | unimplemented | Blown String fuse on input (BLOWN_STRING_FUSE)
[7 empty] | Bit 13 | 1 = Under temperature (UNDER_TEMP) |  |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | unimplemented | 1 = Generic Memory or Communication error (internal) (MEMORY_LOSS)
[7 empty] | unimplemented | 1 = Hardware test failure (HW_TEST_FAILURE)
40112 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | supported |  | R | Reserved for future use
40114 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of active power derating: - Bit0: Power curtailment from external command (NOTE: Asserted also for limitation from capability together with bit 12). - Bit1: Power limitation from Frequency-Watt - Bit2: Power limitation from high average grid voltage - Bit3: Power limitation from anti-islanding protection - Bit4: Power limitation from grid current rating limitation - Bit5: Power limitation for high temperature - Bit6: Power limitation for high DC voltage - Bit7: Reserved - Bit8: Power limitation from ramp-rate (connection ramp) - Bit9: Power limitation from momentary cessation - Bit10: Power limitation from ramp-rate (normal ramp-up) - Bit11: Power limitation from Volt-Watt - Bit12: Power limitation from capability (rating) - Bit13-31: Reserved
40116 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of apparent power derating: - Bit0: Power limitation for high temperature - Bit1: Power limitation for high DC voltage - Bit2: Power limitation from capability (rating) - Bit3-31: Reserved
40118 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of auxiliary devices: - Bit0: Fan fault - Bit1-31: Reserved
40120 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | Fixed to 0 (reserved for future use)

## 103
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40070 | ID | Inverter (Three Phase) |  | uint16 |  |  | 103 |  |  | Include this model for three phase inverter monitoring
40071 | L |  |  | uint16 |  |  | 50 |  |  | Model Length
40072 | A | Amps |  | uint16 | A | A_SF | supported |  | R | AC Current
40073 | AphA | Amps PhaseA |  | uint16 | A | A_SF | supported |  | R | Phase A Current
40074 | AphB | Amps PhaseB |  | uint16 | A | A_SF | supported |  | R | Phase B Current
40075 | AphC | Amps PhaseC |  | uint16 | A | A_SF | supported |  | R | Phase C Current
40076 | A_SF | A_SF |  | sunssf |  |  | -1 |  | R
40077 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | supported |  | R | Phase Voltage AB
40078 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | supported |  | R | Phase Voltage BC
40079 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | supported |  | R | Phase Voltage CA
40080 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | supported |  | R | Phase Voltage AN
40081 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | supported |  | R | Phase Voltage BN
40082 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | supported |  | R | Phase Voltage CN
40083 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R
40084 | W | Watts |  | int16 | W | W_SF | supported |  | R | AC Power
40085 | W_SF | W_SF |  | sunssf |  |  | 1 |  | R
40086 | Hz | Hz |  | uint16 | Hz | Hz_SF | supported |  | R | Line Frequency
40087 | Hz_SF | Hz_SF |  | sunssf |  |  | -2 |  | R
40088 | VA | VA |  | int16 | VA | VA_SF | supported |  | R | AC Apparent Power
40089 | VA_SF | VA_SF |  | sunssf |  |  | 1 |  | R
40090 | Var | Var |  | int16 | var | VAr_SF | supported |  | R | AC Reactive Power
40091 | VAr_SF | VAr_SF |  | sunssf |  |  | 1 |  | R
40092 | PF | PF |  | int16 | Pct | PF_SF | supported |  | R | AC Power Factor | Default: EEI
40093 | PF_SF | PF_SF |  | sunssf |  |  | -4 |  | R
40094 | WH | WattHours |  | acc32 | Wh | WH_SF | supported |  | R | AC Energy | Total Energy is provided on model 122 (ActWh)
40096 | WH_SF | WH_SF |  | sunssf |  |  | 1 |  | R
40097 | DCA | DC Amps |  | uint16 | A | DCA_SF | supported |  | R | DC Current
40098 | DCA_SF | DCA_SF |  | sunssf |  |  | -1 |  | R
40099 | DCV | DC Voltage |  | uint16 | V | DCV_SF | unimplemented |  | R | DC Voltage | For this product the DC voltage is not provided with model 103 but using model 160.
40100 | DCV_SF | DCV_SF |  | sunssf |  |  | unimplemented |  | R
40101 | DCW | DC Watts |  | int16 | W | DCW_SF | supported |  | R | DC Power
40102 | DCW_SF | DCW_SF |  | sunssf |  |  | 1 |  | R
40103 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | supported |  | R | Cabinet Temperature | This measure is implemented as logic board temperature.
40104 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | supported |  | R | Heat Sink Temperature | This measure is implemented as DC/AC (inverter) stage temperature.
40105 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | unimplemented |  | R | Transformer Temperature
40106 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | supported |  | R | Other Temperature | This measure is implemented as DC/DC (inverter) stage temperature.
40107 | Tmp_SF | Tmp_SF |  | sunssf |  |  | -1 |  | R
40108 | St | Operating State |  | enum16 |  |  | supported |  | R | Enumerated value. Operating state
[7 empty] | 1 | Off (OFF) |  |  | This state corresponds to startup phase of inverter controller.
[7 empty] | 2 | Sleeping (SLEEPING) |  |  | This state corresponds to execution of grid interface "auto-test" required by Italian country standard.
[7 empty] | 3 | Starting (STARTING) |  |  | This state corresponds to grid connection phase.
[7 empty] | 4 | MPPT |  |  | This state corresponds to inverter connected to grid and running with MPPT.
[7 empty] | 5 | Throttled (THROTTLED) |  |  | This state corresponds to inverter connected to grid and running with limited active power (derating).
[7 empty] | 6 | Shutting down (SHUTTING_DOWN) |  |  | This state corresponds to forced disconnection from grid (e.g. commanded by user through "remote off" command).
[7 empty] | 7 | Fault (FAULT) |  |  | This state corresponds to fault causing disconnection from grid.
[7 empty] | 8 | Standby (STANDBY) |  |  | This state corresponds to disconnection from grid caused by missing DC source or AC grid.
40109 | StVnd | Vendor Operating State |  | enum16 |  |  | supported |  | R | Vendor specific operating state code
40110 | Evt1 | Event1 |  | bitfield32 |  |  | supported |  | R | Bitmask value. Event fields
[7 empty] | Bit 0 | 1 = Ground fault (GROUND_FAULT) |  |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 = DC over voltage (DC_OVER_VOLT) |  |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | AC disconnect open (AC_DISCONNECT)
[7 empty] | unimplemented | DC disconnect open (DC_DISCONNECT)
[7 empty] | Bit 4 | 1 = Grid shutdown (GRID_DISCONNECT) |  |  | This state corresponds to grid absence.
[7 empty] | unimplemented | Cabinet open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 = Manual shutdown (MANUAL_SHUTDOWN) |  |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 = Over temperature (OVER_TEMP) |  |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | Bit 8 | 1 = Frequency above limit (OVER_FREQUENCY) |  |  | This state corresponds to the following internal alarms: - E006: Grid OF
[7 empty] | Bit 9 | 1 = Frequency under limit (UNDER_FREQUENCY) |  |  | This state corresponds to the following internal alarms: - E007: Grid UF
[7 empty] | Bit 10 | 1 = AC Voltage above limit (AC_OVER_VOLT) |  |  | This state corresponds to the following internal alarms: - E003: Grid OV
[7 empty] | Bit 11 | 1 = AC Voltage under limit (AC_UNDER_VOLT) |  |  | This state corresponds to the following internal alarms: - E004: Grid UV
[7 empty] | unimplemented | Blown String fuse on input (BLOWN_STRING_FUSE)
[7 empty] | Bit 13 | 1 = Under temperature (UNDER_TEMP) |  |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | unimplemented | 1 = Generic Memory or Communication error (internal) (MEMORY_LOSS)
[7 empty] | unimplemented | 1 = Hardware test failure (HW_TEST_FAILURE)
40112 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | supported |  | R | Reserved for future use
40114 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of active power derating: - Bit0: Power curtailment from external command (NOTE: Asserted also for limitation from capability together with bit 12). - Bit1: Power limitation from Frequency-Watt - Bit2: Power limitation from high average grid voltage - Bit3: Power limitation from anti-islanding protection - Bit4: Power limitation from grid current rating limitation - Bit5: Power limitation for high temperature - Bit6: Power limitation for high DC voltage - Bit7: Reserved - Bit8: Power limitation from ramp-rate (connection ramp) - Bit9: Power limitation from momentary cessation - Bit10: Power limitation from ramp-rate (normal ramp-up) - Bit11: Power limitation from Volt-Watt - Bit12: Power limitation from capability (rating) - Bit13-31: Reserved
40116 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of apparent power derating: - Bit0: Power limitation for high temperature - Bit1: Power limitation for high DC voltage - Bit2: Power limitation from capability (rating) - Bit3-31: Reserved
40118 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | This register provides status of auxiliary devices: - Bit0: Fan fault - Bit1-31: Reserved
40120 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | supported |  | R | Vendor defined events | Fixed to 0 (reserved for future use)

## 120
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40122 | ID | Nameplate |  | uint16 |  |  | 120 |  |  | Inverter Controls Nameplate Ratings
40123 | L |  |  | uint16 |  |  | 26 |  |  | Model Length
40124 | DERTyp | DERTyp |  | enum16 |  |  | supported |  | R | Type of DER device. Default value is 4 to indicate PV device.
[7 empty] | 4 | PV
[7 empty] | 82 | PV_STOR
40125 | WRtg | WRtg |  | uint16 | W | WRtg_SF | supported |  | R | Continuous power output capability of the inverter. | WRtg represents the max active power capability of the inverter and cannot be modified. Similar considerations apply to all power ratings below.
40126 | WRtg_SF | WRtg_SF |  | sunssf |  |  | 1 |  | R | Scale factor
40127 | VARtg | VARtg |  | uint16 | VA | VARtg_SF | supported |  | R | Continuous Volt-Ampere capability of the inverter.
40128 | VARtg_SF | VARtg_SF |  | sunssf |  |  | 1 |  | R | Scale factor
40129 | VArRtgQ1 | VArRtgQ1 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 1.
40130 | VArRtgQ2 | VArRtgQ2 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 2.
40131 | VArRtgQ3 | VArRtgQ3 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 3.
40132 | VArRtgQ4 | VArRtgQ4 |  | int16 | var | VArRtg_SF | supported |  | R | Continuous VAR capability of the inverter in quadrant 4.
40133 | VArRtg_SF | VArRtg_SF |  | sunssf |  |  | 1 |  | R | Scale factor
40134 | ARtg | ARtg |  | uint16 | A | ARtg_SF | supported |  | R | Maximum RMS AC current level capability of the inverter. | Used as reference rating for current ramp-rate on M145.
40135 | ARtg_SF | ARtg_SF |  | sunssf |  |  | -1 |  | R | Scale factor
40136 | PFRtgQ1 | PFRtgQ1 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 1. | Default: EEI
40137 | PFRtgQ2 | PFRtgQ2 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 2.
40138 | PFRtgQ3 | PFRtgQ3 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 3.
40139 | PFRtgQ4 | PFRtgQ4 |  | int16 | cos() | PFRtg_SF | supported |  | R | Minimum power factor capability of the inverter in quadrant 4. | Default: EEI
40140 | PFRtg_SF | PFRtg_SF |  | sunssf |  |  | -3 |  | R | Scale factor
40141 | WHRtg | WHRtg |  | uint16 | Wh | WHRtg_SF | unimplemented |  | R | Nominal energy rating of storage device.
40142 | WHRtg_SF | WHRtg_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor
40143 | AhrRtg | AhrRtg |  | uint16 | AH | AhrRtg_SF | unimplemented |  | R | The useable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating).
40144 | AhrRtg_SF | AhrRtg_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for amp-hour rating.
40145 | MaxChaRte | MaxChaRte |  | uint16 | W | MaxChaRte_SF | unimplemented |  | R | Maximum rate of energy transfer into the storage device.
40146 | MaxChaRte_SF | MaxChaRte_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor
40147 | MaxDisChaRte | MaxDisChaRte |  | uint16 | W | MaxDisChaRte_SF | unimplemented |  | R | Maximum rate of energy transfer out of the storage device.
40148 | MaxDisChaRte_SF | MaxDisChaRte_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor
40149 | Pad | Pad |  | pad |  |  |  |  | R | Pad register.

## 121
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40150 | ID | Basic Settings |  | uint16 |  |  | 121 |  |  | Inverter Controls Basic Settings
40151 | L |  |  | uint16 |  |  | 30 |  |  | Model Length
40152 | WMax | WMax |  | uint16 | W | WMax_SF | supported |  | RW | Setting for maximum power output. Default to WRtg. | WMax represents the max active power capability of the inverter; it can be modified (reduced) respect to WRtg and the modification is intended to be done during fine tuning only. WMax is not intended as register to be written for active power control. Set Point for active power WMaxLimPct [group 123] is expressed as percentage of this register, any change on WMax will influence the behavior of active power set point. The max active power used for power control purposes can be calculated as WMax*10^(WMax_SF). Similar considerations apply to all power ratings below. Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40153 | VRef | VRef |  | uint16 | V | VRef_SF | supported |  | RW | Voltage at the PCC.
40154 | VRefOfs | VRefOfs |  | int16 | V | VRefOfs_SF | unimplemented |  | RW | Offset from PCC to inverter.
40155 | VMax | VMax |  | uint16 | V | VMinMax_SF | unimplemented |  | RW | Setpoint for maximum voltage.
40156 | VMin | VMin |  | uint16 | V | VMinMax_SF | unimplemented |  | RW | Setpoint for minimum voltage.
40157 | VAMax | VAMax |  | uint16 | VA | VAMax_SF | supported |  | RW | Setpoint for maximum apparent power. Default to VARtg. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40158 | VArMaxQ1 | VArMaxQ1 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | Since reactive power limit is equally applied on all quadrants, the same parameter value is actually exposed on VArMaxQ1, VArMaxQ2, VArMaxQ3 and VArMaxQ4. This produces the following consequences: - When one of these registers is written, the same value (if accepted) will be read on the others; - When multiple registers are written, only the last change is applied; In addition, if VArMax is changed when VArPct control (M123) is enabled in VArMax mode, it is necessary to disable and enable again the VArPct control or restart the logical controller (e.g. cycling power feed) in order to use the new VArMax limit. Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40159 | VArMaxQ2 | VArMaxQ2 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2.
40160 | VArMaxQ3 | VArMaxQ3 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3.
40161 | VArMaxQ4 | VArMaxQ4 |  | int16 | var | VArMax_SF | supported |  | RW | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4.
40162 | WGra | WGra |  | uint16 | % WMax/sec | WGra_SF | supported |  | RW | Default ramp rate of change of active power due to command or internal action. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40163 | PFMinQ1 | PFMinQ1 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1.
40164 | PFMinQ2 | PFMinQ2 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2.
40165 | PFMinQ3 | PFMinQ3 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3.
40166 | PFMinQ4 | PFMinQ4 |  | int16 | cos() | PFMin_SF | unimplemented |  | RW | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4.
40167 | VArAct | VArAct |  | enum16 |  |  | unimplemented |  | RW | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization.
40168 | ClcTotVA | ClcTotVA |  | enum16 |  |  | unimplemented |  | RW | Calculation method for total apparent power. 1=vector 2=arithmetic.
40169 | MaxRmpRte | MaxRmpRte |  | uint16 | % WGra | MaxRmpRte_SF | unimplemented |  | RW | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.
40170 | ECPNomHz | ECPNomHz |  | uint16 | Hz | ECPNomHz_SF | unimplemented |  | RW | Setpoint for nominal frequency at the ECP.
40171 | ConnPh | ConnPh |  | enum16 |  |  | unimplemented |  | RW | Identity of connected phase for single phase inverters. A=1 B=2 C=3.
40172 | WMax_SF | WMax_SF |  | sunssf |  |  | 1 |  | R | Scale factor for real power.
40173 | VRef_SF | VRef_SF |  | sunssf |  |  | -1 |  | R | Scale factor for voltage at the PCC.
40174 | VRefOfs_SF | VRefOfs_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for offset voltage.
40175 | VMinMax_SF | VMinMax_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for min/max voltages.
40176 | VAMax_SF | VAMax_SF |  | sunssf |  |  | 1 |  | R | Scale factor for apparent power.
40177 | VArMax_SF | VArMax_SF |  | sunssf |  |  | 1 |  | R | Scale factor for reactive power.
40178 | WGra_SF | WGra_SF |  | sunssf |  |  | -1 |  | R | Scale factor for default ramp rate.
40179 | PFMin_SF | PFMin_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for minimum power factor.
40180 | MaxRmpRte_SF | MaxRmpRte_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for maximum ramp percentage.
40181 | ECPNomHz_SF | ECPNomHz_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for nominal frequency.

## 122
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40182 | ID | Measurements_Status |  | uint16 |  |  | 122 |  |  | Inverter Controls Extended Measurements and Status
40183 | L |  |  | uint16 |  |  | 44 |  |  | Model Length
40184 | PVConn | PVConn |  | bitfield16 |  |  | supported |  | R | PV inverter present/available status. Enumerated value.
[7 empty] | Bit 0 | 1 = CONNECTED
[7 empty] | Bit 1 | 1 = AVAILABLE
[7 empty] | unimplemented | OPERATING
[7 empty] | unimplemented | TEST
40185 | StorConn | StorConn |  | bitfield16 |  |  | supported |  | R | Storage inverter present/available status. Enumerated value.
[7 empty] | Bit 0 | 1 = CONNECTED
[7 empty] | Bit 1 | 1 = AVAILABLE
[7 empty] | Bit 2 | 1 = OPERATING
[7 empty] | unimplemented | TEST
40186 | ECPConn | ECPConn |  | bitfield16 |  |  | supported |  | R | ECP connection status: disconnected=0 connected=1.
[7 empty] | Bit 0 | 1 = CONNECTED
40187 | ActWh | ActWh |  | acc64 | Wh |  | supported |  | R | AC lifetime active (real) energy output. | Total exported active energy
40191 | ActVAh | ActVAh |  | acc64 | VAh |  | supported |  | R | AC lifetime apparent energy output. | Total exported apparent energy
40195 | ActVArhQ1 | ActVArhQ1 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime reactive energy output in quadrant 1.
40199 | ActVArhQ2 | ActVArhQ2 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime reactive energy output in quadrant 2.
40203 | ActVArhQ3 | ActVArhQ3 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime negative energy output in quadrant 3.
40207 | ActVArhQ4 | ActVArhQ4 |  | acc64 | varh |  | unimplemented |  | R | AC lifetime reactive energy output in quadrant 4.
40211 | VArAval | VArAval |  | int16 | var | VArAval_SF | unimplemented |  | R | Amount of VARs available without impacting watts output.
40212 | VArAval_SF | VArAval_SF |  | sunssf |  |  | 1 |  | R | Scale factor for available VARs.
40213 | WAval | WAval |  | uint16 | var | WAval_SF | unimplemented |  | R | Amount of Watts available.
40214 | WAval_SF | WAval_SF |  | sunssf |  |  | unimplemented |  | R | Scale factor for available Watts.
40215 | StSetLimMsk | StSetLimMsk |  | bitfield32 |  |  | supported |  | R | Bit Mask indicating setpoint limit(s) reached.
[7 empty] | Bit 0 | 1 = WMax
[7 empty] | Bit 1 | 1 = VAMax
[7 empty] | unimplemented | VArAval
[7 empty] | Bit 3 | 1 = VArMaxQ1 |  |  | Since reactive power operates with the same limit on all quadrants, bits VArMaxQ1, VArMaxQ2, VArMaxQ3, VArMaxQ4 are set together.
[7 empty] | Bit 4 | 1 = VArMaxQ2
[7 empty] | Bit 5 | 1 = VArMaxQ3
[7 empty] | Bit 6 | 1 = VArMaxQ4
[7 empty] | unimplemented | PFMinQ1
[7 empty] | unimplemented | PFMinQ2
[7 empty] | unimplemented | PFMinQ3
[7 empty] | unimplemented | PFMinQ4
40217 | StActCtl | StActCtl |  | bitfield32 | 0 | 0 | supported |  | R | Bit Mask indicating which inverter controls are currently active.
[7 empty] | Bit 0 | 1 = FixedW
[7 empty] | Bit 1 | 1 = FixedVAR
[7 empty] | Bit 2 | 1 = FixedPF
[7 empty] | Bit 3 | Volt-VAr
[7 empty] | unimplemented | Freq-Watt-Param
[7 empty] | unimplemented | Freq-Watt-Curve
[7 empty] | unimplemented | Dyn-Reactive-Current
[7 empty] | unimplemented | LVRT
[7 empty] | unimplemented | HVRT
[7 empty] | Bit 9 | Watt-PF
[7 empty] | Bit 10 | Volt-Watt
[7 empty] | unimplemented | Scheduled
[7 empty] | unimplemented | LFRT
[7 empty] | unimplemented | HFRT
40219 | TmSrc | TmSrc |  | string |  |  | unimplemented |  | R | Source of time synchronization.
40223 | Tms | Tms |  | uint32 | Secs |  | supported |  | R | Seconds since 01-01-2000 00:00 UTC
40225 | RtSt | RtSt |  | bitfield16 |  |  | unimplemented |  | R | Bit Mask indicating active ride-through status.
40226 | Ris | Ris |  | uint16 | ohms | Ris_SF | supported |  | R | Isolation resistance.
40227 | Ris_SF | Ris_SF |  | sunssf |  |  | 3 |  | R | Scale factor for isolation resistance.

## 123
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40228 | ID | Immediate Controls |  | uint16 |  |  | 123 |  |  | Immediate Inverter Controls | i. MaxLimPct: represents the target set-point of the active power control. - The set-point is expressed as % of WMax [group 121]; - The set point is calculated as WMaxLimPct *10^( WMaxLimPct_SF); - The target ouput power of the inverter is then calculated as WMax*10^(WMax_SF)*[WMaxLimPct *10^( WMaxLimPct_SF)]/100. ii. WMaxLimPct_WinTms: the time window is a period of time within which the inverter randomly delays before beginning execution of the command. iii. WMaxLimPct_RvrtTms: the reversion timeout value (if not zero) specifies a time for the requested change to revert to its default state. A timeout value of zero means the change persists until another change is made. If a reversion timer expires the control reverts to its default state. A timeout value of zero shall be avoided for closed loop control purpose. iv. WMaxLimPct_RmpTms: the ramp time is a fixed time in seconds, over which the inverter settings are to transition from their pre—setting level to their post—settings level v. WMaxLim_Ena represents the enable for the active power management according to the previously described 4 registers. WMaxLim_Ena is set at 0 by default and must be written to 1 to enable the active power reduction according to previous registers; In dynamic control funcitioning, the set-point is expected to be updated before the revision time WMaxLimPct_RvrtTms expires. To make effective the new active power settings it is needed to overwrite 1 to the enable WMaxLim_Ena register. Similar considerations apply to reactive power and power factor controls.
40229 | L |  |  | uint16 |  |  | 24 |  |  | Model Length
40230 | Conn_WinTms | Conn_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for connect/disconnect.
40231 | Conn_RvrtTms | Conn_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for connect/disconnect.
40232 | Conn | Conn |  | enum16 |  |  | supported |  | RW | Enumerated valued. Connection control.
[7 empty] | 0 | DISCONNECT
[7 empty] | 1 | CONNECT
40233 | WMaxLimPct | WMaxLimPct |  | uint16 | % WMax | WMaxLimPct_SF | supported |  | RW | Set power output to specified level.
40234 | WMaxLimPct_WinTms | WMaxLimPct_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for power limit change.
40235 | WMaxLimPct_RvrtTms | WMaxLimPct_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for power limit. | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the control settings will be saved on non-volatile storage and so the user application shall not send frequent commands using RvrtTms = 0 because this can damage the memory support.
40236 | WMaxLimPct_RmpTms | WMaxLimPct_RmpTms |  | uint16 | Secs |  | supported |  | RW | Ramp time for moving from current setpoint to new setpoint.
40237 | WMaxLim_Ena | WMaxLim_Ena |  | enum16 |  |  | supported |  | RW | Enumerated valued. Throttle enable/disable control.
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
40238 | OutPFSet | OutPFSet |  | int16 | cos() | OutPFSet_SF | supported |  | RW | Set power factor to specific value - cosine of angle.
40239 | OutPFSet_WinTms | OutPFSet_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for power factor change.
40240 | OutPFSet_RvrtTms | OutPFSet_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for power factor. | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not send frequent commands using RvrtTms = 0 because this can damage the memory support. In case RvtTms > 0 is sent, "default" settings will be restored when reversion time is expired.
40241 | OutPFSet_RmpTms | OutPFSet_RmpTms |  | uint16 | Secs |  | supported |  | RW | Ramp time for moving from current setpoint to new setpoint.
40242 | OutPFSet_Ena | OutPFSet_Ena |  | enum16 |  |  | supported |  | RW | Enumerated valued. Fixed power factor enable/disable control.
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
40243 | VArWMaxPct | VArWMaxPct |  | int16 | % WMax | VArPct_SF | supported |  | RW | Reactive power in percent of WMax. | Before to write and enable this set point, register VArPct_Mod shall be properly configured
40244 | VArMaxPct | VArMaxPct |  | int16 | % VArMax | VArPct_SF | supported |  | RW | Reactive power in percent of VArMax. | Before to write and enable this set point, register VArPct_Mod shall be properly configured
40245 | VArAvalPct | VArAvalPct |  | int16 | % VArAval | VArPct_SF | unimplemented |  | RW | Reactive power in percent of VArAval.
40246 | VArPct_WinTms | VArPct_WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for VAR limit change.
40247 | VArPct_RvrtTms | VArPct_RvrtTms |  | uint16 | Secs |  | supported |  | RW | Timeout period for VAR limit. | Reversion time (RvrtTms) is managed in 60 s units. This means that if a setting value is not a multiple of 60 s, it will be truncated to nearest multiple (e.g. if a value of 90 s is set, a time of 60 s will be actually managed by controller). When reversion time (RvrtTms) value is set to 0, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not send frequent commands using RvrtTms = 0 because this can damage the memory support. In case RvtTms > 0 is sent, "default" settings will be restored when reversion time is expired.
40248 | VArPct_RmpTms | VArPct_RmpTms |  | uint16 | Secs |  | supported |  | RW | Ramp time for moving from current setpoint to new setpoint.
40249 | VArPct_Mod | VArPct_Mod |  | enum16 |  |  | supported |  | RW | Enumerated value. VAR percent limit mode. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
[7 empty] | 0 | NONE |  |  | Default value to NONE. VAMax is used NONE is selected
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40250 | VArPct_Ena | VArPct_Ena |  | enum16 |  |  | supported |  | RW | Enumerated valued. Percent limit VAr enable/disable control.
[7 empty] | 0 | DISABLED
[7 empty] | 1 | ENABLED
40251 | WMaxLimPct_SF | WMaxLimPct_SF |  | sunssf |  |  | -1 |  | R | Scale factor for power output percent.
40252 | OutPFSet_SF | OutPFSet_SF |  | sunssf |  |  | -4 |  | R | Scale factor for power factor.
40253 | VArPct_SF | VArPct_SF |  | sunssf |  |  | -1 |  | R | Scale factor for reactive power percent.

## 126
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40254 | ID | Static Volt-VAR |  | uint16 |  |  | 126 |  |  | Static Volt-VAR Arrays | Monotony of curve: X values (Vn) for Volt-VAR curve must be arranged in a monotonic increasing sequence. Limitation: We can write MAX 2 couple of values (Vx-VArx) at once
40255 | L |  |  | uint16 |  |  | 226 |  |  | Model Length
40256 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40257 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | Is Volt-VAR control active.
[7 empty] | Bit 0 | 1 = ENABLED
40258 | WinTms | WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for volt-VAR change. | WinTms is placed in subsequent address respect to ModEna register. If WinTms is written after having written 1 on ModEna for enabling the control, the new WinTms value is not applied (because the WinTms setting is acquired immediately when control is enabled). This means that the client application must write the desired time on WinTms register before writing 1 on ModEna for enabling the control.
40259 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for volt-VAR curve selection.
40260 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40261 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend 4).
40262 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of curve points supported (maximum of 20).
40263 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40264 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | -1 |  | R | scale factor for dependent variable.
40265 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | 0 |  | R | Scale factor for increment and decrement ramps.
40266 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40267 | DeptRef | DeptRef | 1 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. The convention we adopt is different from Sunspec standard. In our implementation: 0 -> maximum apparent power, 1 -> maximum active power, 2 -> maximum reactive power, 3 (available reactive power) -> NOT SUPPORTED. 0, 1 and 2 are the only values that can be read and written in this register. All the attempts to write different values return "illegal data value" that is modbus exception 3.
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40268 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40269 | VAr1 | VAr1 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40270 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40271 | VAr2 | VAr2 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40272 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40273 | VAr3 | VAr3 | 1 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40274 | V4 | V4 | 1 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40275 | VAr4 | VAr4 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40276 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40277 | VAr5 | VAr5 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40278 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40279 | VAr6 | VAr6 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40280 | V7 | V7 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40281 | VAr7 | VAr7 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40282 | V8 | V8 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40283 | VAr8 | VAr8 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40284 | V9 | V9 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40285 | VAr9 | VAr9 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40286 | V10 | V10 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40287 | VAr10 | VAr10 | 1 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40288 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40289 | VAr11 | VAr11 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40290 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40291 | VAr12 | VAr12 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40292 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40293 | VAr13 | VAr13 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40294 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40295 | VAr14 | VAr14 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40296 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40297 | VAr15 | VAr15 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40298 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40299 | VAr16 | VAr16 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40300 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40301 | VAr17 | VAr17 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40302 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40303 | VAr18 | VAr18 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40304 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40305 | VAr19 | VAr19 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40306 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40307 | VAr20 | VAr20 | 1 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40308 | CrvNam | CrvNam | 1 | string |  |  | model 1 |  | R | Optional description for curve. (Max 16 chars) | Fixed value
40316 | RmpTms |  | 1 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40317 | RmpDecTmm | RmpDecTmm | 1 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40318 | RmpIncTmm | RmpIncTmm | 1 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40319 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
40320 | ActPt | ActPt | 2 | uint16 |  |  | supported |  | RW | Number of active points in array.
40321 | DeptRef | DeptRef | 2 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. The convention we adopt is different from Sunspec standard. In our implementation: 0 -> maximum apparent power, 1 -> maximum active power, 2 -> maximum reactive power, 3 (available reactive power) -> NOT SUPPORTED. 0, 1 and 2 are the only values that can be read and written in this register. All the attempts to write different values return "illegal data value" that is modbus exception 3.
[7 empty] | 1 | Wmax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40322 | V1 | V1 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40323 | VAr1 | VAr1 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40324 | V2 | V2 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40325 | VAr2 | VAr2 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40326 | V3 | V3 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40327 | VAr3 | VAr3 | 2 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40328 | V4 | V4 | 2 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40329 | VAr4 | VAr4 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40330 | V5 | V5 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40331 | VAr5 | VAr5 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40332 | V6 | V6 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40333 | VAr6 | VAr6 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40334 | V7 | V7 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40335 | VAr7 | VAr7 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40336 | V8 | V8 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40337 | VAr8 | VAr8 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40338 | V9 | V9 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40339 | VAr9 | VAr9 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40340 | V10 | V10 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40341 | VAr10 | VAr10 | 2 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40342 | V11 | V11 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40343 | VAr11 | VAr11 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40344 | V12 | V12 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40345 | VAr12 | VAr12 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40346 | V13 | V13 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40347 | VAr13 | VAr13 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40348 | V14 | V14 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40349 | VAr14 | VAr14 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40350 | V15 | V15 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40351 | VAr15 | VAr15 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40352 | V16 | V16 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40353 | VAr16 | VAr16 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40354 | V17 | V17 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40355 | VAr17 | VAr17 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40356 | V18 | V18 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40357 | VAr18 | VAr18 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40358 | V19 | V19 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40359 | VAr19 | VAr19 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40360 | V20 | V20 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40361 | VAr20 | VAr20 | 2 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40362 | CrvNam | CrvNam | 2 | string |  |  | model 2 |  | R | Optional description for curve. (Max 16 chars) | Fixed value
40370 | RmpTms |  | 2 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40371 | RmpDecTmm | RmpDecTmm | 2 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40372 | RmpIncTmm | RmpIncTmm | 2 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40373 | ReadOnly | ReadOnly | 2 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
40374 | ActPt | ActPt | 3 | uint16 |  |  | supported |  | RW | Number of active points in array.
40375 | DeptRef | DeptRef | 3 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. The convention we adopt is different from Sunspec standard. In our implementation: 0 -> maximum apparent power, 1 -> maximum active power, 2 -> maximum reactive power, 3 (available reactive power) -> NOT SUPPORTED. 0, 1 and 2 are the only values that can be read and written in this register. All the attempts to write different values return "illegal data value" that is modbus exception 3.
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40376 | V1 | V1 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40377 | VAr1 | VAr1 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40378 | V2 | V2 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40379 | VAr2 | VAr2 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40380 | V3 | V3 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40381 | VAr3 | VAr3 | 3 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40382 | V4 | V4 | 3 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40383 | VAr4 | VAr4 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40384 | V5 | V5 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40385 | VAr5 | VAr5 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40386 | V6 | V6 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40387 | VAr6 | VAr6 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40388 | V7 | V7 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40389 | VAr7 | VAr7 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40390 | V8 | V8 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40391 | VAr8 | VAr8 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40392 | V9 | V9 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40393 | VAr9 | VAr9 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40394 | V10 | V10 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40395 | VAr10 | VAr10 | 3 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40396 | V11 | V11 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40397 | VAr11 | VAr11 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40398 | V12 | V12 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40399 | VAr12 | VAr12 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40400 | V13 | V13 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40401 | VAr13 | VAr13 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40402 | V14 | V14 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40403 | VAr14 | VAr14 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40404 | V15 | V15 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40405 | VAr15 | VAr15 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40406 | V16 | V16 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40407 | VAr16 | VAr16 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40408 | V17 | V17 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40409 | VAr17 | VAr17 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40410 | V18 | V18 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40411 | VAr18 | VAr18 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40412 | V19 | V19 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40413 | VAr19 | VAr19 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40414 | V20 | V20 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40415 | VAr20 | VAr20 | 3 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40416 | CrvNam | CrvNam | 3 | string |  |  | model 3 |  | R | Optional description for curve. (Max 16 chars) | Fixed value
40424 | RmpTms |  | 3 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40425 | RmpDecTmm | RmpDecTmm | 3 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40426 | RmpIncTmm | RmpIncTmm | 3 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40427 | ReadOnly | ReadOnly | 3 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
40428 | ActPt | ActPt | 4 | uint16 |  |  | supported |  | RW | Number of active points in array.
40429 | DeptRef | DeptRef | 4 | enum16 |  | DeptRef_SF | supported |  | RW | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. The convention we adopt is different from Sunspec standard. In our implementation: 0 -> maximum apparent power, 1 -> maximum active power, 2 -> maximum reactive power, 3 (available reactive power) -> NOT SUPPORTED. 0, 1 and 2 are the only values that can be read and written in this register. All the attempts to write different values return "illegal data value" that is modbus exception 3.
[7 empty] | 1 | WMax
[7 empty] | 2 | VArMax
[7 empty] | unimplemented | VArAval
40430 | V1 | V1 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40431 | VAr1 | VAr1 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 1 VARs.
40432 | V2 | V2 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40433 | VAr2 | VAr2 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 2 VARs.
40434 | V3 | V3 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40435 | VAr3 | VAr3 | 4 | int16 | Various | DeptRef_SF | supported |  | RW | Point 3 VARs.
40436 | V4 | V4 | 4 | uint16 |  | V_SF | supported |  | RW | Point 4 Volts.
40437 | VAr4 | VAr4 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 4 VARs.
40438 | V5 | V5 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40439 | VAr5 | VAr5 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 5 VARs.
40440 | V6 | V6 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40441 | VAr6 | VAr6 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 6 VARs.
40442 | V7 | V7 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40443 | VAr7 | VAr7 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 7 VARs.
40444 | V8 | V8 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40445 | VAr8 | VAr8 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 8 VARs.
40446 | V9 | V9 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40447 | VAr9 | VAr9 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 9 VARs.
40448 | V10 | V10 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40449 | VAr10 | VAr10 | 4 | int16 |  | DeptRef_SF | supported |  | RW | Point 10 VARs.
40450 | V11 | V11 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40451 | VAr11 | VAr11 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 11 VARs.
40452 | V12 | V12 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40453 | VAr12 | VAr12 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 12 VARs.
40454 | V13 | V13 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40455 | VAr13 | VAr13 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 13 VARs.
40456 | V14 | V14 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40457 | VAr14 | VAr14 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 14 VARs.
40458 | V15 | V15 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40459 | VAr15 | VAr15 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 15 VARs.
40460 | V16 | V16 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40461 | VAr16 | VAr16 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 16 VARs.
40462 | V17 | V17 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40463 | VAr17 | VAr17 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 17 VARs.
40464 | V18 | V18 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40465 | VAr18 | VAr18 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 18 VARs.
40466 | V19 | V19 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40467 | VAr19 | VAr19 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 19 VARs.
40468 | V20 | V20 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40469 | VAr20 | VAr20 | 4 | int16 |  | DeptRef_SF | unimplemented |  | RW | Point 20 VARs.
40470 | CrvNam | CrvNam | 4 | string |  |  | model 4 |  | R | Optional description for curve. (Max 16 chars) | Fixed value
40478 | RmpTms |  | 4 | uint16 | Secs |  | unimplemented |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%).
40479 | RmpDecTmm | RmpDecTmm | 4 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40480 | RmpIncTmm | RmpIncTmm | 4 | uint16 | % ref_value/min | RmpIncDec_SF | unimplemented |  | RW | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
40481 | ReadOnly | ReadOnly | 4 | enum16 |  |  | supported |  | R | Boolean flag indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 127
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40482 | ID | Freq-Watt Param |  | uint16 |  |  | 127 |  |  | Parameterized Frequency-Watt
40483 | L |  |  | uint16 |  |  | 10 |  |  | Model Length
40484 | WGra | WGra |  | uint16 | % PM/Hz | WGra_SF | supported |  | RW | The slope of the reduction in the maximum allowed watts output as a function of frequency. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40485 | HzStr | HzStr |  | int16 | Hz | HzStrStop_SF | supported |  | RW | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs.
40486 | HzStop | HzStop |  | int16 | Hz | HzStrStop_SF | supported |  | RW | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed.
40487 | HysEna | HysEna |  | bitfield16 |  |  | supported |  | RW | Enable hysterisis
[7 empty] | Bit 0 | 1 = ENABLED
40488 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | Is Parameterized Frequency-Watt control active.
[7 empty] | Bit 0 | 1 = ENABLED
40489 | HzStopWGra | HzStopWGra |  | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event.
40490 | WGra_SF | WGra_SF |  | sunssf |  |  | 0 |  | R | Scale factor for output gradient.
40491 | HzStrStop_SF | HzStrStop_SF |  | sunssf |  |  | -2 |  | R | Scale factor for frequency deviations.
40492 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | 0 |  | R | Scale factor for increment and decrement ramps.
40493 | Pad |  |  | pad |  |  |  |  | R

## 129
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40494 | ID | LVRTD |  | uint16 |  |  | 129 |  |  | LVRT Must Disconnect
40495 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40496 | ActCrv | ActCrv |  | uint16 |  |  | 1 |  | R | Index of active curve. 0=no active curve. | Fixed value (0=no active curve not implemented)
40497 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. ModEna = 0 (Stepwise Protection): Protection thresholds and trip times operate as discrete step functions. Values remain constant between consecutive setpoints. ModEna = 1 (Time-Variant Protection): Enables dynamic protection. Trip times and thresholds are linearly interpolated between any two consecutive coordinate points, resulting in a continuous slope rather than a step change.
[7 empty] | Bit 0 | 1 = ENABLED
40498 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for LVRT change.
40499 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for LVRT curve selection.
40500 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40501 | NCrv | NCrv |  | uint16 |  |  | 1 |  | R | Number of curves supported (recommend 4). | Fixed value
40502 | NPt | NPt |  | uint16 |  |  | 6 |  | R | Number of curve points supported (maximumn of 20). | Fixed value
40503 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40504 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40505 | Pad |  |  | pad |  |  |  |  | R
40506 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40507 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40508 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 must disconnect voltage.
40509 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40510 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 must disconnect voltage.
40511 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40512 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 must disconnect voltage.
40513 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40514 | V4 | V4 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 must disconnect voltage.
40515 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40516 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 must disconnect voltage.
40517 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40518 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 must disconnect voltage.
40519 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40520 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 must disconnect voltage.
40521 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40522 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 must disconnect voltage.
40523 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40524 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 must disconnect voltage.
40525 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40526 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 must disconnect voltage.
40527 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40528 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 must disconnect voltage.
40529 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40530 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 must disconnect voltage.
40531 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40532 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 must disconnect voltage.
40533 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40534 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 must disconnect voltage.
40535 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40536 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 must disconnect voltage.
40537 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40538 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 must disconnect voltage.
40539 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40540 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 must disconnect voltage.
40541 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40542 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 must disconnect voltage.
40543 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40544 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 must disconnect voltage.
40545 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40546 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 must disconnect voltage.
40547 | CrvNam | CrvNam | 1 | string |  |  | model 1 |  | R | Optional description for curve. | Fixed value
40555 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 130
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40556 | ID | HVRTD |  | uint16 |  |  | 130 |  |  | HVRT Must Disconnect
40557 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40558 | ActCrv | ActCrv |  | uint16 |  |  | 1 |  | R | Index of active curve. 0=no active curve. | Fixed value (0=no active curve not implemented)
40559 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | HVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. ModEna = 0 (Stepwise Protection): Protection thresholds and trip times operate as discrete step functions. Values remain constant between consecutive setpoints. ModEna = 1 (Time-Variant Protection): Enables dynamic protection. Trip times and thresholds are linearly interpolated between any two consecutive coordinate points, resulting in a continuous slope rather than a step change.
[7 empty] | Bit 0 | 1 = ENABLED
40560 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for HVRT change.
40561 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for HVRT curve selection.
40562 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40563 | NCrv | NCrv |  | uint16 |  |  | 1 |  | R | Number of curves supported (recommend 4). | Fixed value
40564 | NPt | NPt |  | uint16 |  |  | 6 |  | R | Number of curve points supported (maximumn of 20). | Fixed value
40565 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40566 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40567 | Pad |  |  | pad |  |  |  |  | R
40568 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40569 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40570 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 must disconnect voltage.
40571 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40572 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 must disconnect voltage.
40573 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40574 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 must disconnect voltage.
40575 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40576 | V4 | V4 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 must disconnect voltage.
40577 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40578 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 must disconnect voltage.
40579 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40580 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 must disconnect voltage.
40581 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40582 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 must disconnect voltage.
40583 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40584 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 must disconnect voltage.
40585 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40586 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 must disconnect voltage.
40587 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40588 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 must disconnect voltage.
40589 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40590 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 must disconnect voltage.
40591 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40592 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 must disconnect voltage.
40593 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40594 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 must disconnect voltage.
40595 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40596 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 must disconnect voltage.
40597 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40598 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 must disconnect voltage.
40599 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40600 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 must disconnect voltage.
40601 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40602 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 must disconnect voltage.
40603 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40604 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 must disconnect voltage.
40605 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40606 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 must disconnect voltage.
40607 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40608 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 must disconnect voltage.
40609 | CrvNam | CrvNam | 1 | string |  |  | model 1 |  | R | Optional description for curve. | Fixed value
40617 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 132
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40618 | ID | Volt-Watt |  | uint16 |  |  | 132 |  |  | Volt-Watt | Monotony of curve: X values (Vn) for Volt-Watt curve must be arranged in a monotonic increasing sequence. Limitation: We can write MAX 2 couple of values (Vx-Wx) at once
40619 | L |  |  | uint16 |  |  | 226 |  |  | Model Length
40620 | ActCrv | ActCrv |  | uint16 |  |  | supported |  | RW | Index of active curve. 0=no active curve. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40621 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | Is Volt-Watt control active.
[7 empty] | Bit 0 | 1 = ENABLED
40622 | WinTms | WinTms |  | uint16 | Secs |  | supported |  | RW | Time window for volt-watt change. | WinTms is placed in subsequent address respect to ModEna register. If WinTms is written after having written 1 on ModEna for enabling the control, the new WinTms value is not applied (because the WinTms setting is acquired immediately when control is enabled). This means that the client application must write the desired time on WinTms register before writing 1 on ModEna for enabling the control.
40623 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for volt-watt curve selection.
40624 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40625 | NCrv | NCrv |  | uint16 |  |  | supported |  | R | Number of curves supported (recommend min. 4).
40626 | NPt | NPt |  | uint16 |  |  | supported |  | R | Number of points in array (maximum 20).
40627 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40628 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | -1 |  | R | Scale Factor for % DeptRef
40629 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | 0 |  | R | Scale factor for increment and decrement ramps.
40630 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40631 | DeptRef | DeptRef | 1 | enum16 |  |  | 1 |  | R | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Fixed value
[7 empty] | 1 | %WMax
[7 empty] | unimplemented | %WAval
40632 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40633 | W1 | W1 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40634 | V2 | V2 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40635 | W2 | W2 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40636 | V3 | V3 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40637 | W3 | W3 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40638 | V4 | V4 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40639 | W4 | W4 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40640 | V5 | V5 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40641 | W5 | W5 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40642 | V6 | V6 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40643 | W6 | W6 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40644 | V7 | V7 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40645 | W7 | W7 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40646 | V8 | V8 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40647 | W8 | W8 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40648 | V9 | V9 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40649 | W9 | W9 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40650 | V10 | V10 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40651 | W10 | W10 | 1 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40652 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40653 | W11 | W11 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40654 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40655 | W12 | W12 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40656 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40657 | W13 | W13 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40658 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40659 | W14 | W14 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40660 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40661 | W15 | W15 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40662 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40663 | W16 | W16 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40664 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40665 | W17 | W17 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40666 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40667 | W18 | W18 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40668 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40669 | W19 | W19 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40670 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40671 | W20 | W20 | 1 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40672 | CrvNam | CrvNam | 1 | string |  |  | model 1 |  | R | Optional description for curve. | Fixed value
40680 | RmpPt1Tms | RmpPt1Tms | 1 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40681 | RmpDecTmm | RmpDecTmm | 1 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40682 | RmpIncTmm | RmpIncTmm | 1 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40683 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY
40684 | ActPt | ActPt | 2 | uint16 |  |  | supported |  | RW | Number of active points in array.
40685 | DeptRef | DeptRef | 2 | enum16 |  |  | 1 |  | R | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Fixed value
[7 empty] | 1 | %WMax
[7 empty] | unimplemented | %WAval
40686 | V1 | V1 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40687 | W1 | W1 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40688 | V2 | V2 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40689 | W2 | W2 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40690 | V3 | V3 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40691 | W3 | W3 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40692 | V4 | V4 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40693 | W4 | W4 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40694 | V5 | V5 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40695 | W5 | W5 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40696 | V6 | V6 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40697 | W6 | W6 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40698 | V7 | V7 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40699 | W7 | W7 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40700 | V8 | V8 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40701 | W8 | W8 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40702 | V9 | V9 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40703 | W9 | W9 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40704 | V10 | V10 | 2 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40705 | W10 | W10 | 2 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40706 | V11 | V11 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40707 | W11 | W11 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40708 | V12 | V12 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40709 | W12 | W12 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40710 | V13 | V13 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40711 | W13 | W13 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40712 | V14 | V14 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40713 | W14 | W14 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40714 | V15 | V15 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40715 | W15 | W15 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40716 | V16 | V16 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40717 | W16 | W16 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40718 | V17 | V17 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40719 | W17 | W17 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40720 | V18 | V18 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40721 | W18 | W18 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40722 | V19 | V19 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40723 | W19 | W19 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40724 | V20 | V20 | 2 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40725 | W20 | W20 | 2 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40726 | CrvNam | CrvNam | 2 | string |  |  | model 2 |  | R | Optional description for curve. | Fixed value
40734 | RmpPt1Tms | RmpPt1Tms | 2 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40735 | RmpDecTmm | RmpDecTmm | 2 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40736 | RmpIncTmm | RmpIncTmm | 2 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40737 | ReadOnly | ReadOnly | 2 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
40738 | ActPt | ActPt | 3 | uint16 |  |  | supported |  | RW | Number of active points in array.
40739 | DeptRef | DeptRef | 3 | enum16 |  |  | 1 |  | R | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Fixed value
[7 empty] | 1 | %WMax
[7 empty] | unimplemented | %WAval
40740 | V1 | V1 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40741 | W1 | W1 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40742 | V2 | V2 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40743 | W2 | W2 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40744 | V3 | V3 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40745 | W3 | W3 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40746 | V4 | V4 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40747 | W4 | W4 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40748 | V5 | V5 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40749 | W5 | W5 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40750 | V6 | V6 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40751 | W6 | W6 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40752 | V7 | V7 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40753 | W7 | W7 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40754 | V8 | V8 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40755 | W8 | W8 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40756 | V9 | V9 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40757 | W9 | W9 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40758 | V10 | V10 | 3 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40759 | W10 | W10 | 3 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40760 | V11 | V11 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40761 | W11 | W11 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40762 | V12 | V12 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40763 | W12 | W12 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40764 | V13 | V13 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40765 | W13 | W13 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40766 | V14 | V14 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40767 | W14 | W14 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40768 | V15 | V15 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40769 | W15 | W15 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40770 | V16 | V16 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40771 | W16 | W16 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40772 | V17 | V17 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40773 | W17 | W17 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40774 | V18 | V18 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40775 | W18 | W18 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40776 | V19 | V19 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40777 | W19 | W19 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40778 | V20 | V20 | 3 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40779 | W20 | W20 | 3 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40780 | CrvNam | CrvNam | 3 | string |  |  | model 3 |  | R | Optional description for curve. | Fixed value
40788 | RmpPt1Tms | RmpPt1Tms | 3 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40789 | RmpDecTmm | RmpDecTmm | 3 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40790 | RmpIncTmm | RmpIncTmm | 3 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40791 | ReadOnly | ReadOnly | 3 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
40792 | ActPt | ActPt | 4 | uint16 |  |  | supported |  | RW | Number of active points in array.
40793 | DeptRef | DeptRef | 4 | enum16 |  |  | 1 |  | R | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | Fixed value
[7 empty] | 1 | %WMax
[7 empty] | unimplemented | %WAval
40794 | V1 | V1 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 Volts. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40795 | W1 | W1 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 1 Watts.
40796 | V2 | V2 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 2 Volts.
40797 | W2 | W2 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 2 Watts.
40798 | V3 | V3 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 3 Volts.
40799 | W3 | W3 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 3 Watts.
40800 | V4 | V4 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 4 Volts.
40801 | W4 | W4 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 4 Watts.
40802 | V5 | V5 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 5 Volts.
40803 | W5 | W5 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 5 Watts.
40804 | V6 | V6 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 6 Volts.
40805 | W6 | W6 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 6 Watts.
40806 | V7 | V7 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 7 Volts.
40807 | W7 | W7 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 7 Watts.
40808 | V8 | V8 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 8 Volts.
40809 | W8 | W8 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 8 Watts.
40810 | V9 | V9 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 9 Volts.
40811 | W9 | W9 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 9 Watts.
40812 | V10 | V10 | 4 | uint16 | % VRef | V_SF | supported |  | RW | Point 10 Volts.
40813 | W10 | W10 | 4 | int16 | % VRef | DeptRef_SF | supported |  | RW | Point 10 Watts.
40814 | V11 | V11 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 Volts.
40815 | W11 | W11 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 11 Watts.
40816 | V12 | V12 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 Volts.
40817 | W12 | W12 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 12 Watts.
40818 | V13 | V13 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 Volts.
40819 | W13 | W13 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 13 Watts.
40820 | V14 | V14 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 Volts.
40821 | W14 | W14 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 14 Watts.
40822 | V15 | V15 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 Volts.
40823 | W15 | W15 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 15 Watts.
40824 | V16 | V16 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 Volts.
40825 | W16 | W16 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 16 Watts.
40826 | V17 | V17 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 Volts.
40827 | W17 | W17 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 17 Watts.
40828 | V18 | V18 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 Volts.
40829 | W18 | W18 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 18 Watts.
40830 | V19 | V19 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 Volts.
40831 | W19 | W19 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 19 Watts.
40832 | V20 | V20 | 4 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 Volts.
40833 | W20 | W20 | 4 | int16 | % VRef | DeptRef_SF | unimplemented |  | RW | Point 20 Watts.
40834 | CrvNam | CrvNam | 4 | string |  |  | model 4 |  | R | Optional description for curve. | Fixed value
40842 | RmpPt1Tms | RmpPt1Tms | 4 | uint16 | Secs |  | supported |  | RW | The time of the PT1 in seconds (time to accomplish a change of 95%). | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40843 | RmpDecTmm | RmpDecTmm | 4 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
40844 | RmpIncTmm | RmpIncTmm | 4 | uint16 | % WMax/min | RmpIncDec_SF | supported |  | RW | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
40845 | ReadOnly | ReadOnly | 4 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.

## 135
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40846 | ID | LFRT |  | uint16 |  |  | 135 |  |  | Low Frequency Ride-through
40847 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40848 | ActCrv | ActCrv |  | uint16 |  |  | 1 |  | R | Index of active curve. 0=no active curve. | Fixed value (0=no active curve not implemented)
40849 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LFRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. ModEna = 0 (Stepwise Protection): Protection thresholds and trip times operate as discrete step functions. Values remain constant between consecutive setpoints. ModEna = 1 (Time-Variant Protection): Enables dynamic protection. Trip times and thresholds are linearly interpolated between any two consecutive coordinate points, resulting in a continuous slope rather than a step change.
[7 empty] | Bit 0 | 1 = ENABLED
40850 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for LFRT change.
40851 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for LFRT curve selection.
40852 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40853 | NCrv | NCrv |  | uint16 |  |  | 1 |  | R | Number of curves supported (recommend 4). | Fixed value
40854 | NPt | NPt |  | uint16 |  |  | 6 |  | R | Number of curve points supported (maximumn of 20). | Fixed value
40855 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40856 | Hz_SF | Hz_SF |  | sunssf |  |  | -4 |  | R | Scale factor for frequency.
40857 | Pad |  |  | pad |  |  |  |  | R
40858 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40859 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40860 | Hz1 | Hz1 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 1 must disconnect frequency.
40861 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40862 | Hz2 | Hz2 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 2 must disconnect frequency.
40863 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40864 | Hz3 | Hz3 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 3 must disconnect frequency.
40865 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40866 | Hz4 | Hz4 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 4 must disconnect frequency.
40867 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40868 | Hz5 | Hz5 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 5 must disconnect frequency.
40869 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40870 | Hz6 | Hz6 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 6 must disconnect frequency.
40871 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40872 | Hz7 | Hz7 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 7 must disconnect frequency.
40873 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40874 | Hz8 | Hz8 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 8 must disconnect frequency.
40875 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40876 | Hz9 | Hz9 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 9 must disconnect frequency.
40877 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40878 | Hz10 | Hz10 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 10 must disconnect frequency.
40879 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40880 | Hz11 | Hz11 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 11 must disconnect frequency.
40881 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40882 | Hz12 | Hz12 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 12 must disconnect frequency.
40883 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40884 | Hz13 | Hz13 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 13 must disconnect frequency.
40885 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40886 | Hz14 | Hz14 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 14 must disconnect frequency.
40887 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40888 | Hz15 | Hz15 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 15 must disconnect frequency.
40889 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40890 | Hz16 | Hz16 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 16 must disconnect frequency.
40891 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40892 | Hz17 | Hz17 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 17 must disconnect frequency.
40893 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40894 | Hz18 | Hz18 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 18 must disconnect frequency.
40895 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40896 | Hz19 | Hz19 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 19 must disconnect frequency.
40897 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40898 | Hz20 | Hz20 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 20 must disconnect frequency.
40899 | CrvNam | CrvNam | 1 | string |  |  | model 1 |  | R | Optional description for curve. | Fixed value
40907 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 136
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40908 | ID | HFRT |  | uint16 |  |  | 136 |  |  | High Frequency Ride-through
40909 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40910 | ActCrv | ActCrv |  | uint16 |  |  | 1 |  | R | Index of active curve. 0=no active curve. | Fixed value (0=no active curve not implemented)
40911 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | HFRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. ModEna = 0 (Stepwise Protection): Protection thresholds and trip times operate as discrete step functions. Values remain constant between consecutive setpoints. ModEna = 1 (Time-Variant Protection): Enables dynamic protection. Trip times and thresholds are linearly interpolated between any two consecutive coordinate points, resulting in a continuous slope rather than a step change.
[7 empty] | Bit 0 | 1 = ENABLED
40912 | WinTms | WinTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Time window for HFRT change.
40913 | RvrtTms | RvrtTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Timeout period for HFRT curve selection.
40914 | RmpTms | RmpTms |  | uint16 | Secs | 0 | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40915 | NCrv | NCrv |  | uint16 |  |  | 1 |  | R | Number of curves supported (recommend 4). | Fixed value
40916 | NPt | NPt |  | uint16 |  |  | 6 |  | R | Number of curve points supported (maximumn of 20). | Fixed value
40917 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40918 | Hz_SF | Hz_SF |  | sunssf |  |  | -4 |  | R | Scale factor for frequency.
40919 | Pad |  |  | pad |  |  |  |  | R
40920 | ActPt | ActPt | 1 | uint16 |  |  | supported |  | RW | Number of active points in array.
40921 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 1 must disconnect duration. | Whenever a write operation change the value of these registers, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40922 | Hz1 | Hz1 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 1 must disconnect frequency.
40923 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 2 must disconnect duration.
40924 | Hz2 | Hz2 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 2 must disconnect frequency.
40925 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 3 must disconnect duration.
40926 | Hz3 | Hz3 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 3 must disconnect frequency.
40927 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 4 must disconnect duration.
40928 | Hz4 | Hz4 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 4 must disconnect frequency.
40929 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 5 must disconnect duration.
40930 | Hz5 | Hz5 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 5 must disconnect frequency.
40931 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | supported |  | RW | Point 6 must disconnect duration.
40932 | Hz6 | Hz6 | 1 | uint16 | Hz | Hz_SF | supported |  | RW | Point 6 must disconnect frequency.
40933 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 must disconnect duration.
40934 | Hz7 | Hz7 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 7 must disconnect frequency.
40935 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 must disconnect duration.
40936 | Hz8 | Hz8 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 8 must disconnect frequency.
40937 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 must disconnect duration.
40938 | Hz9 | Hz9 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 9 must disconnect frequency.
40939 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 must disconnect duration.
40940 | Hz10 | Hz10 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 10 must disconnect frequency.
40941 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 must disconnect duration.
40942 | Hz11 | Hz11 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 11 must disconnect frequency.
40943 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 must disconnect duration.
40944 | Hz12 | Hz12 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 12 must disconnect frequency.
40945 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 must disconnect duration.
40946 | Hz13 | Hz13 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 13 must disconnect frequency.
40947 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 must disconnect duration.
40948 | Hz14 | Hz14 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 14 must disconnect frequency.
40949 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 must disconnect duration.
40950 | Hz15 | Hz15 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 15 must disconnect frequency.
40951 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 must disconnect duration.
40952 | Hz16 | Hz16 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 16 must disconnect frequency.
40953 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 must disconnect duration.
40954 | Hz17 | Hz17 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 17 must disconnect frequency.
40955 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 must disconnect duration.
40956 | Hz18 | Hz18 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 18 must disconnect frequency.
40957 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 must disconnect duration.
40958 | Hz19 | Hz19 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 19 must disconnect frequency.
40959 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 must disconnect duration.
40960 | Hz20 | Hz20 | 1 | uint16 | Hz | Hz_SF | unimplemented |  | RW | Point 20 must disconnect frequency.
40961 | CrvNam | CrvNam | 1 | string |  |  | model 1 |  | R | Optional description for curve. | Fixed value
40969 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 139
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
40970 | ID | LVRTX |  | uint16 |  |  | 139 |  |  | LVRT extended curve
40971 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
40972 | ActCrv | ActCrv |  | uint16 |  |  | 1 |  | R | Index of active curve. 0=no active curve. | Fixed value (0=no active curve not implemented)
40973 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. ModEna = 1: Enables the LVRT Cease to Energize (Momentary Cessation) function. When active, the inverter stops exporting power during a voltage disturbance without disconnecting from the grid.
[7 empty] | Bit 0 | 1 = ENABLED |  |  | The enable of LVRT is shared with HVRT so setting this bit has the same effect on "ModEna" register of M140.
40974 | WinTms | WinTms |  | uint16 | Secs |  | unimplemented |  | RW | Time window for LVRT change.
40975 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for LVRT curve selection.
40976 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
40977 | NCrv | NCrv |  | uint16 |  |  | 1 |  | R | Number of curves supported (recommend 4). | Fixed value
40978 | NPt | NPt |  | uint16 |  |  | 1 |  | R | Number of curve points supported (maximumn of 20). | Fixed value
40979 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
40980 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
40981 | CrvType |  |  | enum16 |  |  | 1 |  | R |  | Fixed value
[7 empty] | 1 | CEASE_TO_ENERGIZE
40982 | ActPt | ActPt | 1 | uint16 |  |  | 1 |  | RW | Number of active points in array. | Fixed value
40983 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 1 duration.
40984 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 voltage. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
40985 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 2 duration.
40986 | V2 | V2 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 2 voltage.
40987 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 3 duration.
40988 | V3 | V3 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 3 voltage.
40989 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 4 duration.
40990 | V4 | V4 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 4 voltage.
40991 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 5 duration.
40992 | V5 | V5 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 5 voltage.
40993 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 6 duration.
40994 | V6 | V6 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 6 voltage.
40995 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 duration.
40996 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 voltage.
40997 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 duration.
40998 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 voltage.
40999 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 duration.
41000 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 voltage.
41001 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 duration.
41002 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 voltage.
41003 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 duration.
41004 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 voltage.
41005 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 duration.
41006 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 voltage.
41007 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 duration.
41008 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 voltage.
41009 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 duration.
41010 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 voltage.
41011 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 duration.
41012 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 voltage.
41013 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 duration.
41014 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 voltage.
41015 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 duration.
41016 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 voltage.
41017 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 duration.
41018 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 voltage.
41019 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 duration.
41020 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 voltage.
41021 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 duration.
41022 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 voltage.
41023 | CrvNam | CrvNam | 1 | string |  |  | model 1 |  | R | Optional description for curve. | Fixed value
41031 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 140
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
41032 | ID | HVRTX |  | uint16 |  |  | 140 |  |  | HVRT extended curve
41033 | L |  |  | uint16 |  |  | 60 |  |  | Model Length
41034 | ActCrv | ActCrv |  | uint16 |  |  | 1 |  | R | Index of active curve. 0=no active curve. | Fixed value (0=no active curve not implemented)
41035 | ModEna | ModEna |  | bitfield16 |  |  | supported |  | RW | LVRT control mode. Enable active curve. Bitfield value. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support. ModEna = 1: Enables the LVRT Cease to Energize (Momentary Cessation) function. When active, the inverter stops exporting power during a voltage disturbance without disconnecting from the grid.
[7 empty] | Bit 0 | 1 = ENABLED |  |  | The enable of HVRT is shared with LVRT so setting this bit has the same effect on "ModEna" register of M139.
41036 | WinTms | WinTms |  | uint16 | Secs |  | unimplemented |  | RW | Time window for LVRT change.
41037 | RvrtTms | RvrtTms |  | uint16 | Secs |  | unimplemented |  | RW | Timeout period for LVRT curve selection.
41038 | RmpTms | RmpTms |  | uint16 | Secs |  | unimplemented |  | RW | Ramp time for moving from current mode to new mode.
41039 | NCrv | NCrv |  | uint16 |  |  | 1 |  | R | Number of curves supported (recommend 4). | Fixed value
41040 | NPt | NPt |  | uint16 |  |  | 1 |  | R | Number of curve points supported (maximumn of 20). | Fixed value
41041 | Tms_SF | Tms_SF |  | sunssf |  |  | -2 |  | R | Scale factor for duration.
41042 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale factor for percent VRef.
41043 | CrvType |  |  | enum16 |  |  | 1 |  | R |  | Fixed value
[7 empty] | 1 | CEASE_TO_ENERGIZE
41044 | ActPt | ActPt | 1 | uint16 |  |  | 1 |  | R | Number of active points in array. | Fixed value
41045 | Tms1 | Tms1 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 1 duration.
41046 | V1 | V1 | 1 | uint16 | % VRef | V_SF | supported |  | RW | Point 1 voltage. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
41047 | Tms2 | Tms2 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 2 duration.
41048 | V2 | V2 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 2 voltage.
41049 | Tms3 | Tms3 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 3 duration.
41050 | V3 | V3 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 3 voltage.
41051 | Tms4 | Tms4 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 4 duration.
41052 | V4 | V4 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 4 voltage.
41053 | Tms5 | Tms5 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 5 duration.
41054 | V5 | V5 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 5 voltage.
41055 | Tms6 | Tms6 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 6 duration.
41056 | V6 | V6 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 6 voltage.
41057 | Tms7 | Tms7 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 7 duration.
41058 | V7 | V7 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 7 voltage.
41059 | Tms8 | Tms8 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 8 duration.
41060 | V8 | V8 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 8 voltage.
41061 | Tms9 | Tms9 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 9 duration.
41062 | V9 | V9 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 9 voltage.
41063 | Tms10 | Tms10 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 10 duration.
41064 | V10 | V10 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 10 voltage.
41065 | Tms11 | Tms11 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 11 duration.
41066 | V11 | V11 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 11 voltage.
41067 | Tms12 | Tms12 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 12 duration.
41068 | V12 | V12 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 12 voltage.
41069 | Tms13 | Tms13 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 13 duration.
41070 | V13 | V13 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 13 voltage.
41071 | Tms14 | Tms14 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 14 duration.
41072 | V14 | V14 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 14 voltage.
41073 | Tms15 | Tms15 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 15 duration.
41074 | V15 | V15 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 15 voltage.
41075 | Tms16 | Tms16 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 16 duration.
41076 | V16 | V16 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 16 voltage.
41077 | Tms17 | Tms17 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 17 duration.
41078 | V17 | V17 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 17 voltage.
41079 | Tms18 | Tms18 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 18 duration.
41080 | V18 | V18 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 18 voltage.
41081 | Tms19 | Tms19 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 19 duration.
41082 | V19 | V19 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 19 voltage.
41083 | Tms20 | Tms20 | 1 | uint16 | Secs | Tms_SF | unimplemented |  | RW | Point 20 duration.
41084 | V20 | V20 | 1 | uint16 | % VRef | V_SF | unimplemented |  | RW | Point 20 voltage.
41085 | CrvNam | CrvNam | 1 | string |  |  | model 1 |  | R | Optional description for curve. | Fixed value
41093 | ReadOnly | ReadOnly | 1 | enum16 |  |  | supported |  | R | Enumerated value indicates if curve is read-only or can be modified.
[7 empty] | 0 | READWRITE
[7 empty] | unimplemented | READONLY

## 145
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
41094 | ID | Extended Settings |  | uint16 |  |  | 145 |  |  | Inverter controls extended settings
41095 | L | [5 empty] | 8 |  |  | Model Length
41096 | NomRmpUpRte | Ramp Up Rate |  | uint16 | Pct | Rmp_SF | supported |  | RW | Ramp up rate as a percentage of max current. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
41097 | NomRmpDnRte | NomRmpDnRte |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Ramp down rate as a percentage of max current.
41098 | EmgRmpUpRte | Emergency Ramp Up Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Emergency ramp down rate as a percentage of max current.
41099 | EmgRmpDnRte | Emergency Ramp Down Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Emergency ramp down rate as a percentage of max current.
41100 | ConnRmpUpRte | Connect Ramp Up Rate |  | uint16 | Pct | Rmp_SF | supported |  | RW | Connect ramp up rate as a percentage of max current. | Whenever a write operation change the value of this register, the associated control settings will be applied permanently as new "default" values. In this case the control settings will be saved on non-volatile storage and so the user application shall not write continuously a different value because this can damage the memory support.
41101 | ConnRmpDnRte | Connect Ramp Down Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Connect ramp down rate as a percentage of max current.
41102 | AGra | Default Ramp Rate |  | uint16 | Pct | Rmp_SF | unimplemented |  | RW | Ramp rate specified in percent of max current.
41103 | Rmp_SF | Rmp_SF |  | sunssf |  |  | -1 |  | R | Ramp Rate Scale Factor

## 160
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
41104 | ID | Multiple MPPT Inverter Extension Model |  | uint16 |  |  | 160 |  |  |  | Configuration of MPPT channels: Target product supports vendor-specific configuration of MPPT channels, also known as "input mode". The following configuration modes are supported: - 2_mppt: A separate MPPT control runs on each channel so state conditions (e.g. "DCSt" register on M160 repeating blocks) are independent. - 1_mppt: Channel are connected in parallel to the same source and a unique MPPT control runs.
41105 | L |  |  | uint16 |  |  | 48
41106 | DCA_SF | DCA_SF |  | sunssf |  |  | -1 |  | R |  | Current Scale Factor
41107 | DCV_SF | DCV_SF |  | sunssf |  |  | -1 |  | R |  | Voltage Scale Factor
41108 | DCW_SF | DCW_SF |  | sunssf |  |  | 1 |  | R |  | Power Scale Factor
41109 | DCWH_SF | DCWH_SF |  | sunssf |  |  | unimplemented |  | R |  | Energy Scale Factor
41110 | Evt | Global Events |  | bitfield32 |  |  | supported |  | R
[7 empty] | Bit 0 | 1 = Ground Fault (GROUND_FAULT) |  |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 = Input Over Voltage (INPUT_OVER_VOLTAGE) |  |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | Reserved (RESERVED)
[7 empty] | unimplemented | DC Disconnect (DC_DISCONNECT)
[7 empty] | unimplemented | Cabinet Open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 = Manual Shutdown (MANUAL_SHUTDOWN) |  |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 = Over Temperature (OVER_TEMP) |  |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | unimplemented | Blown Fuse (BLOWN_FUSE)
[7 empty] | Bit 13 | 1 = Under Temperature (UNDER_TEMP) |  |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | unimplemented | 1 = Memory Loss (MEMORY_LOSS)
[7 empty] | Bit 15 | 1 = Arc Detection (ARC_DETECTION) |  |  | This state corresponds to the following internal alarms: - E050: Arc-Fault
[7 empty] | unimplemented | 1 = Test Failed (TEST_FAILED)
[7 empty] | unimplemented | 1 = Under Voltage (INPUT_UNDER_VOLTAGE)
[7 empty] | unimplemented | 1 = Over Current (INPUT_OVER_CURRENT)
41112 | N | Number of Modules |  | count |  |  | supported |  | R
41113 | TmsPer | Timestamp Period |  | uint16 |  |  | unimplemented |  | R
41114 | ID | Input ID | 1 | uint16 |  |  | supported |  | R
41115 | IDStr | Input ID Sting | 1 | string |  |  | supported |  | R
41123 | DCA | DC Current | 1 | uint16 | A | DCA_SF | supported |  | R
41124 | DCV | DC Voltage | 1 | uint16 | V | DCV_SF | supported |  | R
41125 | DCW | DC Power | 1 | uint16 | W | DCW_SF | supported |  | R
41126 | DCWH | Lifetime Energy | 1 | acc32 | Wh | DCWH_SF | unimplemented |  | R
41128 | Tms | Timestamp | 1 | uint32 | Secs |  | unimplemented |  | R
41130 | Tmp | Temperature | 1 | int16 | C |  | unimplemented |  | R
41131 | DCSt | Operating State | 1 | enum16 |  |  | supported |  | R
[7 empty] | 1 | Off (OFF) |  |  | This state corresponds to unloaded/disconnected DC channel.
[7 empty] | 2 | Sleeping (SLEEPING) |  |  | This state corresponds to connected DC channel but not ready for starting MPPT (e.g. for low voltage condition).
[7 empty] | 3 | Starting (STARTING) |  |  | This state corresponds to connected DC channel starting MPPT regulation.
[7 empty] | 4 | MPPT |  |  | This state corresponds to connected DC channel running MPPT regulation.
[7 empty] | 5 | Throttled (THROTTLED) |  |  | This state corresponds to connected DC channel with forced MPPT suspension (e,g, for by-pass or power-saving purposes).
[7 empty] | unimplemented | Shutting Down (SHUTTING_DOWN)
[7 empty] | 7 | Fault (FAULT) |  |  | This state corresponds to connected DC channel with pending fault (under-voltage, over-voltage, over-current).
[7 empty] | unimplemented | Standby (STANDBY)
[7 empty] | unimplemented | Test (TEST)
[7 empty] | unimplemented | Reserved (RESERVED)
41132 | DCEvt | Module Events | 1 | bitfield32 |  |  | supported |  | R
[7 empty] | Bit 0 | 1 = Ground Fault (GROUND_FAULT) |  |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 = Input Over Voltage (INPUT_OVER_VOLTAGE) |  |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | Reserved (RESERVED)
[7 empty] | unimplemented | DC Disconnect (DC_DISCONNECT)
[7 empty] | unimplemented | Cabinet Open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 = Manual Shutdown (MANUAL_SHUTDOWN) |  |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 = Over Temperature (OVER_TEMP) |  |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | unimplemented | Blown Fuse (BLOWN_FUSE)
[7 empty] | Bit 13 | 1 = Under Temperature (UNDER_TEMP) |  |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | unimplemented | 1 = Memory Loss (MEMORY_LOSS)
[7 empty] | Bit 15 | 1 = Arc Detection (ARC_DETECTION) |  |  | This state corresponds to the following internal alarms: - E050: Arc-Fault
[7 empty] | unimplemented | 1 = Test Failed (TEST_FAILED)
[7 empty] | Bit 21 | 1 = Under Voltage (INPUT_UNDER_VOLTAGE) |  |  | This state corresponds to the following internal alarms: - W002: Input UV
[7 empty] | Bit 22 | 1 = Over Current (INPUT_OVER_CURRENT) |  |  | This state corresponds to the following internal alarms: - E001: Input OC
41134 | ID | Input ID | 2 | uint16 |  |  | supported |  | R
41135 | IDStr | Input ID Sting | 2 | string |  |  | supported |  | R
41143 | DCA | DC Current | 2 | uint16 | A | DCA_SF | supported |  | R
41144 | DCV | DC Voltage | 2 | uint16 | V | DCV_SF | supported |  | R
41145 | DCW | DC Power | 2 | uint16 | W | DCW_SF | supported |  | R
41146 | DCWH | Lifetime Energy | 2 | acc32 | Wh | DCWH_SF | unimplemented |  | R
41148 | Tms | Timestamp | 2 | uint32 | Secs |  | unimplemented |  | R
41150 | Tmp | Temperature | 2 | int16 | C |  | unimplemented |  | R
41151 | DCSt | Operating State | 2 | enum16 |  |  | supported |  | R
[7 empty] | 1 | Off (OFF) |  |  | This state corresponds to unloaded/disconnected DC channel.
[7 empty] | 2 | Sleeping (SLEEPING) |  |  | This state corresponds to connected DC channel but not ready for starting MPPT (e.g. for low voltage condition).
[7 empty] | 3 | Starting (STARTING) |  |  | This state corresponds to connected DC channel starting MPPT regulation.
[7 empty] | 4 | MPPT |  |  | This state corresponds to connected DC channel running MPPT regulation.
[7 empty] | 5 | Throttled (THROTTLED) |  |  | This state corresponds to connected DC channel with forced MPPT suspension (e,g, for by-pass or power-saving purposes).
[7 empty] | unimplemented | Shutting Down (SHUTTING_DOWN)
[7 empty] | 7 | Fault (FAULT) |  |  | This state corresponds to connected DC channel with pending fault (under-voltage, over-voltage, over-current).
[7 empty] | unimplemented | Standby (STANDBY)
[7 empty] | unimplemented | Test (TEST)
[7 empty] | unimplemented | Reserved (RESERVED)
41152 | DCEvt | Module Events | 2 | bitfield32 |  |  | supported |  | R
[7 empty] | Bit 0 | 1 = Ground Fault (GROUND_FAULT) |  |  | This state corresponds to the following internal alarms: - E018: Leakage current fault - E025: Low R-iso - E037: Grounding interface fault
[7 empty] | Bit 1 | 1 = Input Over Voltage (INPUT_OVER_VOLTAGE) |  |  | This state corresponds to the following internal alarms: - E002: Input OV
[7 empty] | unimplemented | Reserved (RESERVED)
[7 empty] | unimplemented | DC Disconnect (DC_DISCONNECT)
[7 empty] | unimplemented | Cabinet Open (CABINET_OPEN)
[7 empty] | Bit 6 | 1 = Manual Shutdown (MANUAL_SHUTDOWN) |  |  | This state corresponds to the following internal alarms: - E035: Remote off
[7 empty] | Bit 7 | 1 = Over Temperature (OVER_TEMP) |  |  | This state corresponds to the following internal alarms: - E014: OTH
[7 empty] | unimplemented | Blown Fuse (BLOWN_FUSE)
[7 empty] | Bit 13 | 1 = Under Temperature (UNDER_TEMP) |  |  | This state corresponds to the following internal alarms: - E033: UTH
[7 empty] | unimplemented | 1 = Memory Loss (MEMORY_LOSS)
[7 empty] | Bit 15 | 1 = Arc Detection (ARC_DETECTION) |  |  | This state corresponds to the following internal alarms: - E050: Arc-Fault
[7 empty] | unimplemented | 1 = Test Failed (TEST_FAILED)
[7 empty] | Bit 21 | 1 = Under Voltage (INPUT_UNDER_VOLTAGE) |  |  | This state corresponds to the following internal alarms: - W002: Input UV
[7 empty] | Bit 22 | 1 = Over Current (INPUT_OVER_CURRENT) |  |  | This state corresponds to the following internal alarms: - E001: Input OC

## 65233
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
41154 | ID | Multiple Meter |  | uint16 |  |  | 65233 |  |  | Multiple Meter vendor model
41155 | L | L |  | uint16 |  |  | 183 |  |  | Model Length
41156 | RatioTrns_SF | RatioTrns_SF |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Transformers Ratio
41157 | V_SF | V_SF |  | sunssf |  |  | -1 |  | R | Scale Factor for Voltage
41158 | A_SF | A_SF |  | sunssf |  |  | -1 |  | R | Scale Factor for Current
41159 | W_SF | W_SF |  | sunssf |  |  | 1 |  | R | Scale Factor for Active Power
41160 | VAr_SF | VAr_SF |  | sunssf |  |  | 1 |  | R | Scale Factor for Reactive Power
41161 | VA_SF | VA_SF |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Apparent Power
41162 | PF_SF | PF_SF |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Power Factor
41163 | Hz_SF | Hz_SF |  | sunssf |  |  | -2 |  | R | Scale Factor for Frequency
41164 | WH_SF | WH_SF |  | sunssf |  |  | 1 |  | R | Scale Factor for Active Energy
41165 | VArH_SF | VArH_SF |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Reactive Energy
41166 | Thd_SF | Thd_SF |  | sunssf |  |  | unimplemented |  | R | Scale Factor for Total Harmonic Distorsion
41167 | N | Number of modules |  | uint16 |  |  | supported |  | R | Number of meter
41168 | Pos | Meter insertion position | 1 | enum16 |  |  | unimplemented |  | R | Position of meter
41169 | InsMod | Meter grid insertion mode | 1 | enum16 |  |  | supported |  | R | Meter connected phases
[7 empty] | 0 | L123 |  | Meter inserted on all phases
[7 empty] | 1 | L1 |  | Meter inserted on individual phase L1
[7 empty] | 2 | L2 |  | Meter inserted on individual phase L2
[7 empty] | 3 | L3 |  | Meter inserted on individual phase L3
41170 | Mn | Manufacturer | 1 | string |  |  | supported |  | R | Manufacturer specific value
41186 | Md | Model | 1 | string |  |  | supported |  | R | Manufacturer specific value
41202 | Opt | Options | 1 | string |  |  | unimplemented |  | R | Manufacturer specific value
41210 | Vr | Version | 1 | string |  |  | supported |  | R | Manufacturer specific value
41218 | SN | Serial Number | 1 | string |  |  | supported |  | R | Manufacturer specific value
41234 | DA | Device Address | 1 | uint16 |  |  | supported |  | R | Modbus device address
41235 | IP_ADD | IP Address | 1 | uint32 |  |  | unimplemented |  | R | Device IP address
41237 | Sign | Energy measure sign | 1 | enum16 |  |  | unimplemented |  | R | CT Reverse option enabled
41238 | RatioTrnsA | Current transformer ratio | 1 | uint16 |  |  | unimplemented |  | R | Current transformer ratio
41239 | RatioTrnsV | Voltage transformer ratio | 1 | uint16 |  |  | unimplemented |  | R | Voltage transformer ratio
41240 | PPVph12 | Phase Voltage L1-L2 | 1 | uint16 |  |  | unimplemented |  | R | Phase to Phase Voltage L1-L2
41241 | PPVph23 | Phase Voltage L2-L3 | 1 | uint16 |  |  | unimplemented |  | R | Phase to Phase Voltage L1-L3
41242 | PPVph13 | Phase Voltage L3-L1 | 1 | uint16 |  |  | unimplemented |  | R | Phase to Phase Voltage L3-L1
41243 | PhVph1 | Phase Voltage L1-N | 1 | uint16 | V | V_SF | supported |  | R | Phase to Neutral Voltage L1
41244 | PhVph2 | Phase Voltage L2-N | 1 | uint16 | V | V_SF | supported |  | R | Phase to Neutral Voltage L2
41245 | PhVph3 | Phase Voltage L3-N | 1 | uint16 | V | V_SF | supported |  | R | Phase to Neutral Voltage L3
41246 | Aph1 | Amps Phase L1 | 1 | uint16 | A | A_SF | supported |  | R | Total Current on Phase L1
41247 | Aph2 | Amps Phase L2 | 1 | uint16 | A | A_SF | supported |  | R | Total Current on Phase L2
41248 | Aph3 | Amps Phase L3 | 1 | uint16 | A | A_SF | supported |  | R | Total Current on Phase L3
41249 | A | Amps | 1 | uint16 |  |  | unimplemented |  | R | Total Current
41250 | Wph1 | Watts L1 | 1 | int16 | W | W_SF | supported |  | R | Total Active Power on Phase L1
41251 | Wph2 | Watts L2 | 1 | int16 | W | W_SF | supported |  | R | Total Active Power on Phase L2
41252 | Wph3 | Watts L3 | 1 | int16 | W | W_SF | supported |  | R | Total Active Power on Phase L3
41253 | W | Watts | 1 | int16 | W | W_SF | supported |  | R | Total Active Power
41254 | VArph1 | Reactive Power L1 | 1 | int16 | VAr | VAr_SF | supported |  | R | Total Reactive Power on Phase L1
41255 | VArph2 | Reactive Power L2 | 1 | int16 | VAr | VAr_SF | supported |  | R | Total Reactive Power on Phase L2
41256 | VArph3 | Reactive Power L3 | 1 | int16 | VAr | VAr_SF | supported |  | R | Total Reactive Power on Phase L3
41257 | VAr | Reactive Power | 1 | int16 | VAr | VAr_SF | supported |  | R | Total Reactive Power
41258 | VAph1 | Apparent Power L1 | 1 | int16 |  |  | unimplemented |  | R | Total Apparent Power on Phase L1
41259 | VAph2 | Apparent Power L2 | 1 | int16 |  |  | unimplemented |  | R | Total Apparent Power on Phase L2
41260 | VAph3 | Apparent Power L3 | 1 | int16 |  |  | unimplemented |  | R | Total Apparent Power on Phase L3
41261 | VA | Apparent Power | 1 | int16 |  |  | unimplemented |  | R | Total Apparent Power
41262 | PF1 | PF L1 | 1 | int16 |  |  | unimplemented |  | R | Power Factor on Phase L1
41263 | PF2 | PF L2 | 1 | int16 |  |  | unimplemented |  | R | Power Factor on Phase L2
41264 | PF3 | PF L3 | 1 | int16 |  |  | unimplemented |  | R | Power Factor on Phase L3
41265 | PF | PF | 1 | int16 |  |  | unimplemented |  | R | Overall Power Factor
41266 | Hz | Grid frequency | 1 | uint16 | Hz | Hz_SF | supported |  | R | Grid frequency
41267 | WHimp | Active Imported Energy | 1 | acc64 |  |  | unimplemented |  | R | Total Active Imported Energy
41271 | WHexp | Active Exported Energy | 1 | acc64 |  |  | unimplemented |  | R | Total Active Exported Energy
41275 | WHimp1 | Active Imported Energy L1 | 1 | acc64 |  |  | unimplemented |  | R | Active Imported Energy on Phase L1
41279 | WHimp2 | Active Imported Energy L2 | 1 | acc64 |  |  | unimplemented |  | R | Active Imported Energy on Phase L2
41283 | WHimp3 | Active Imported Energy L3 | 1 | acc64 |  |  | unimplemented |  | R | Active Imported Energy on Phase L3
41287 | WHexp1 | Active Exported Energy L1 | 1 | acc64 |  |  | unimplemented |  | R | Active Exported Energy on Phase L1
41291 | WHexp2 | Active Exported Energy L2 | 1 | acc64 |  |  | unimplemented |  | R | Active Exported Energy on Phase L2
41295 | WHexp3 | Active Exported Energy L3 | 1 | acc64 |  |  | unimplemented |  | R | Active Exported Energy on Phase L3
41299 | VArHimp | Reactive Imported Energy | 1 | acc64 |  |  | unimplemented |  | R | Total Reactive Imported Energy
41303 | VArHexp | Reactive Exported Energy | 1 | acc64 |  |  | unimplemented |  | R | Total Reactive Exported Energy
41307 | VArHimp1 | Reactive Imported Energy L1 | 1 | acc64 |  |  | unimplemented |  | R | Reactive Imported Energy on Phase L1
41311 | VArHimp2 | Reactive Exported Energy L1 | 1 | acc64 |  |  | unimplemented |  | R | Reactive Imported Energy on Phase L2
41315 | VArHimp3 | Reactive Imported Energy L2 | 1 | acc64 |  |  | unimplemented |  | R | Reactive Imported Energy on Phase L3
41319 | VArHexp1 | Reactive Exported Energy L2 | 1 | acc64 |  |  | unimplemented |  | R | Reactive Exported Energy on Phase L1
41323 | VArHexp2 | Reactive Imported Energy L3 | 1 | acc64 |  |  | unimplemented |  | R | Reactive Exported Energy on Phase L2
41327 | VArHexp3 | Reactive Exported Energy L3 | 1 | acc64 |  |  | unimplemented |  | R | Reactive Exported Energy on Phase L3
41331 | ThdV1 | Total voltage harmonic distortion % L1 | 1 | uint16 |  |  | unimplemented |  | R | Total voltage harmonic distortion % on Phase L1
41332 | ThdV2 | Total voltage harmonic distortion % L2 | 1 | uint16 |  |  | unimplemented |  | R | Total voltage harmonic distortion % on Phase L2
41333 | ThdV3 | Total voltage harmonic distortion % L3 | 1 | uint16 |  |  | unimplemented |  | R | Total voltage harmonic distortion % on Phase L3
41334 | ThdV | Total voltage harmonic distortion % | 1 | uint16 |  |  | unimplemented |  | R | Overall voltage harmonic distortion %
41335 | ThdA1 | Total current harmonic distortion % L1 | 1 | uint16 |  |  | unimplemented |  | R | Total current harmonic distortion % on Phase L1
41336 | ThdA2 | Total current harmonic distortion % L2 | 1 | uint16 |  |  | unimplemented |  | R | Total current harmonic distortion % on Phase L2
41337 | ThdA3 | Total current harmonic distortion % L3 | 1 | uint16 |  |  | unimplemented |  | R | Total current harmonic distortion % on Phase L3
41338 | ThdA | Total current harmonic distortion % | 1 | uint16 |  |  | unimplemented |  | R | Overall current harmonic distortion %

## 65234
Address | Name | Label | Index | Type | Units | SF | Value | Subvalue | R/W | Description from RefModel | Conformance Notes
41339 | ID | Battery Data |  |  |  |  | 65234 |  |  | Battery Data
41340 | L | [5 empty] | 255
41341 | V_SF | V_SF |  | sunssf |  |  | -2 |  | R | Voltage Scale Factor
41342 | A_SF | A_SF |  | sunssf |  |  | -1 |  | R | Current Scale Factor
41343 | W_SF | W_SF |  | sunssf |  |  | 0 |  | R | Power Scale Factor
41344 | Tmp_SF | Tmp_SF |  | sunssf |  |  | -1 |  | R | Temperature Scale Factor
41345 | SoC_SF | SoC_SF |  | sunssf |  |  | 0 |  | R | State of Charge (SoC) Scale Factor
41346 | SoH_SF | SoH_SF |  | sunssf |  |  | 0 |  | R | State of Health (SoH) Scale Factor
41347 | WH_SF | WH_SF |  | sunssf |  |  | 0 |  | R | Energy Scale Factor
41348 | AH_SF | AH_SF |  | sunssf |  |  | 0 |  | R | Charge Scale Factor
41349 | N | Number of Battery units |  | uint16 |  |  | supported |  | R | Number of Battery units
41350 | SoC | State Of Charge (SoC) |  | uint16 | Pct | SoC_SF | supported |  | R | State Of Charge (SoC) | average of battery units SOC
41351 | W | Total Batteries power |  | int16 | W | W_SF | supported |  | R | Total Batteries power | sum of battery powers
41352 | Mn | Manufacturer | 1 | string |  |  | FIMER |  | R | Manufacturer
41368 | Md | Model | 1 | string |  |  | supported |  | R | Model
41400 | Opt | Options | 1 | string |  |  | unimplemented |  | R | Options
41408 | Vr | Version | 1 | string |  |  | supported |  | R | Version
41424 | SN | Serial Number | 1 | string |  |  | supported |  | R | Serial Number
41440 | BEvt | Battery unit Events | 1 | bitfield32 |  |  | unimplemented |  | R | Battery unit Events
41442 | BA | Current - Battery unit | 1 | int16 | A | A_SF | supported |  | R | Current - Battery unit
41443 | BV | Voltage - Battery unit | 1 | uint32 | V | V_SF | supported |  | R | Voltage - Battery unit
41445 | BW | Power - Battery unit | 1 | int16 | W | W_SF | supported |  | R | Power - Battery unit
41446 | TmpCh | charger Temperature - Battery unit | 1 | uint16 | ℃ | Tmp_SF | unimplemented |  | R | charger Temperature - Battery unit
41447 | BSoC | State of Charge - Battery unit | 1 | uint16 | Pct | SoC_SF | supported |  | R | State of Charge - Battery unit
41448 | VcellMax | Max cell voltage - Battery unit | 1 | uint16 | V | V_SF | unimplemented |  | R | Max cell voltage - Battery unit
41449 | VcellMin | Min cell voltage - Battery unit | 1 | uint16 | V | V_SF | unimplemented |  | R | Min cell voltage - Battery unit
41450 | TmpCellMax | Max cell temperature - Battery unit | 1 | uint16 | ℃ | Tmp_SF | supported |  | R | Max cell temperature - Battery unit
41451 | TmpCellMin | Min cell temperature - Battery unit | 1 | uint16 | ℃ | Tmp_SF | supported |  | R | Min cell temperature - Battery unit
41452 | SoH | State of Health - Battery unit | 1 | uint16 | Pct | SoH_SF | supported |  | R | State of Health - Battery unit
41453 | SHU | Last time of health check - Battery unit | 1 | acc64 (uint64) | Secs |  | unimplemented |  | R | Last time of health check - Battery unit
41457 | WChMax | Max charge power (lifetime) - Battery unit | 1 | uint16 | W | W_SF | supported |  | R | Max charge power (lifetime) - Battery unit
41458 | WDischMax | Max discharge power (lifetime) - Battery unit | 1 | uint16 | W | W_SF | supported |  | R | Max discharge power (lifetime) - Battery unit
41459 | ChTms | Charging time (lifetime) - Battery unit | 1 | uint32 | Secs |  | unimplemented |  | R | Charging time (lifetime) - Battery unit
41461 | DischTms | Discharging time (lifetime) - Battery unit | 1 | uint32 | Secs |  | unimplemented |  | R | Discharging time (lifetime) - Battery unit
41463 | FullAH |  | 1 | uint16 | AH | AH_SF | unimplemented |  | R
41464 | WHCh | Energy charged (Lifetime) - Battery unit | 1 | acc64 | WH | WH_SF | supported |  | R | Energy charged (Lifetime) - Battery unit
41468 | WHDisch | Energy discharged (Lifetime) - Battery unit | 1 | acc64 | WH | WH_SF | supported |  | R | Energy discharged (Lifetime) - Battery unit
41472 | Cycles | Cycle count - Battery unit | 1 | uint32 |  |  | unimplemented |  | R | Cycle count - Battery unit
41474 | Pad | Pad | 1 | pad | [5 empty] | Pad
41475 | Mn | Manufacturer | 2 | string |  |  | FIMER |  | R | Manufacturer
41491 | Md | Model | 2 | string |  |  | supported |  | R | Model
41523 | Opt | Options | 2 | string |  |  | unimplemented |  | R | Options
41531 | Vr | Version | 2 | string |  |  | supported |  | R | Version
41547 | SN | Serial Number | 2 | string |  |  | supported |  | R | Serial Number
41563 | BEvt | Battery unit Events | 2 | bitfield32 |  |  | unimplemented |  | R | Battery unit Events
41565 | BA | Current - Battery unit | 2 | int16 | A | A_SF | supported |  | R | Current - Battery unit
41566 | BV | Voltage - Battery unit | 2 | uint32 | V | V_SF | supported |  | R | Voltage - Battery unit
41568 | BW | Power - Battery unit | 2 | int16 | W | W_SF | supported |  | R | Power - Battery unit
41569 | TmpCh | charger Temperature - Battery unit | 2 | uint16 | ℃ | Tmp_SF | unimplemented |  | R | charger Temperature - Battery unit
41570 | BSoC | State of Charge - Battery unit | 2 | uint16 | Pct | SoC_SF | supported |  | R | State of Charge - Battery unit
41571 | VcellMax | Max cell voltage - Battery unit | 2 | uint16 | V | V_SF | unimplemented |  | R | Max cell voltage - Battery unit
41572 | VcellMin | Min cell voltage - Battery unit | 2 | uint16 | V | V_SF | unimplemented |  | R | Min cell voltage - Battery unit
41573 | TmpCellMax | Max cell temperature - Battery unit | 2 | uint16 | ℃ | Tmp_SF | supported |  | R | Max cell temperature - Battery unit
41574 | TmpCellMin | Min cell temperature - Battery unit | 2 | uint16 | ℃ | Tmp_SF | supported |  | R | Min cell temperature - Battery unit
41575 | SoH | State of Health - Battery unit | 2 | uint16 | Pct | SoH_SF | supported |  | R | State of Health - Battery unit
41576 | SHU | Last time of health check - Battery unit | 2 | acc64 (uint64) | Secs |  | unimplemented |  | R | Last time of health check - Battery unit
41580 | WChMax | Max charge power (lifetime) - Battery unit | 2 | uint16 | W | W_SF | supported |  | R | Max charge power (lifetime) - Battery unit
41581 | WDischMax | Max discharge power (lifetime) - Battery unit | 2 | uint16 | W | W_SF | supported |  | R | Max discharge power (lifetime) - Battery unit
41582 | ChTms | Charging time (lifetime) - Battery unit | 2 | uint32 | Secs |  | unimplemented |  | R | Charging time (lifetime) - Battery unit
41584 | DischTms | Discharging time (lifetime) - Battery unit | 2 | uint32 | Secs |  | unimplemented |  | R | Discharging time (lifetime) - Battery unit
41586 | FullAH | Full charge capacity - Battery unit | 2 | uint16 | AH | AH_SF | unimplemented |  | R
41587 | WHCh | Energy charged (Lifetime) - Battery unit | 2 | acc64 | WH | WH_SF | supported |  | R | Energy charged (Lifetime) - Battery unit
41591 | WHDisch | Energy discharged (Lifetime) - Battery unit | 2 | acc64 | WH | WH_SF | supported |  | R | Energy discharged (Lifetime) - Battery unit
41595 | Cycles | Cycle count - Battery unit | 2 | uint32 |  |  | unimplemented |  | R | Cycle count - Battery unit
41597 | Pad | Pad | 2 | pad | [5 empty] | Pad